## Datasheet(5-4)3P
Submersible Motor Pump Data Sheet
1 | Model | PSS-5-4_MS4-0533 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 24 | m | Discharge Piece | STS304
10 | Rated Capacity | 80 | ℓ/min | Impeller | STS304
11 | Shut off Head | 34 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 50 | % | Pump Shaft | STS431
14 | Min. Flow | 40 | ℓ/min | Coupling | STS304
15 | Max. Flow | 120 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 40 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Sumoto |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 0.37 | kW | Stud | Low Carbon Steel
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 1.8 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Cover | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 153 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 4 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 251 | mm | Pump | 2 | kg
37 | Motor | 235 | mm | Motor | 5.8 | kg
38 | Total | 486 | mm | Total | 7.8 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(5-5)3P
Submersible Motor Pump Data Sheet
1 | Model | PSS-5-5_MS4-0733 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 31 | m | Discharge Piece | STS304
10 | Rated Capacity | 80 | ℓ/min | Impeller | STS304
11 | Shut off Head | 46 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 50 | % | Pump Shaft | STS431
14 | Min. Flow | 40 | ℓ/min | Coupling | STS304
15 | Max. Flow | 140 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 40 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Sumoto |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 0.55 | kW | Stud | Low Carbon Steel
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 2.5 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Cover | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 153 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 5 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 272 | mm | Pump | 2.2 | kg
37 | Motor | 250 | mm | Motor | 7 | kg
38 | Total | 522 | mm | Total | 9.2 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(5-26)
Submersible Motor Pump Data Sheet
1 | Model | PSS-5-26_MS4-5533 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 170 | m | Discharge Piece | STS304
10 | Rated Capacity | 80 | ℓ/min | Impeller | STS304
11 | Shut off Head | 230 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 40 | ℓ/min | Coupling | STS304
15 | Max. Flow | 140 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 40 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Sumoto |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 4 | kW | Stud | Low Carbon Steel
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 11.2 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Cover | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 663 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 26 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 713 | mm | Pump | 6.2 | kg
37 | Motor | 555 | mm | Motor | 23.4 | kg
38 | Total | 1268 | mm | Total | 29.6 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
DIEMENSION(mm)
MODEL | MOTOR | P.L |  |  | M.L |  |  | T.L
PSS-5-4 | MS4-0533 | 251 |  |  | 235 |  |  | 486
PSS-5-5 | MS4-0733 | 272 |  |  | 250 |  |  | 522
PSS-5-26 | MS4-5533 | 713 |  |  | 555 |  |  | 1268
WEIGHT(kg)
MODEL | MOTOR | PUMP |  |  | MOTOR |  |  | TOTAL
PSS-5-4 | MS4-0533 | 2 |  |  | 5.8 |  |  | 7.8
PSS-5-5 | MS4-0733 | 2.2 |  |  | 7 |  |  | 9.2
PSS-5-26 | MS4-5533 | 6.2 |  |  | 23.4 |  |  | 29.6
※MOTOR MAKER : SUMOTO
※DISCHARGE CONNECTION : 1 1/2" (40mm)
|  |  | TYPE |  |  | SUBMERSIBLE PUMP
MODEL
SERVICE
|  |  | SCALE:N/S |  |  |  | 3rd. ANGLE PROJECT
Outline Drawing
of PSS-5 Series
98mm
P.L
M.L
T.L
P.L
M.L
T.L
Cable Guard Included

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO | PART NAME |  |  | MATERIAL |  | Q'TY
1 | Discharge piece |  |  | STS304 |  | 1
2 | Screw |  |  | - |  | 1
3 | Valve guide |  |  | - |  | 1
4 | Valve cone |  |  | STS304 |  | 1
5 | Valve seat |  |  | NBR |  | 1
6 | Valve casing |  |  | STS304 |  | 1
7 | Stop ring |  |  |  |  | 1
8 | Lock nut |  |  |  |  | 1
9 | Stop ring washer |  |  |  |  | 1
10 | Impeller |  |  |  |  | Stages
11 | Neck ring |  |  | NBR |  | Stages
12 | Bearing |  |  |  |  | Stages
13 | Diffuser |  |  | STS304 |  | Stages
14 | Spacer |  |  | - |  | 1
15 | Pump shaft/coupling |  |  | *STS431/304 |  | 1
16 | Strainer |  |  | STS304 |  | 1
17 | Suction interconnector |  |  |  |  | 1
18 | Screw |  |  | - |  | 4
19 | Washer |  |  | STS304 |  | 4
20 | Strap |  |  |  |  | 4
21 | Cable GUARD |  |  |  |  | 1
22 | Check valve |  |  | - |  | 1
23 | Diffuseer Assy |  |  | - |  | Stages
24 | Strainer Assy |  |  | - |  | 1
|  | TYPE |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
Sectional Drawing
of PSS-5 Series

## Test Report(5-4)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 30 | 60 | 80 | 120 | 151
Dis. Head | (m) | 36 | 32.5 | 28.6 | 24.9 | 13.5 | 0.5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0080772 | 0.032309 | 0.057438 | 0.12924 | 0.20463
Total Head | (m) | 37 | 33.5081 | 29.6323 | 25.9574 | 14.6292 | 1.7046
Water Power | (㎾) | 0 | 0.16385 | 0.2898 | 0.33848 | 0.28615 | 0.041956
Shaft Power | (㎾) | 0.24304 | 0.37138 | 0.48856 | 0.54188 | 0.55986 | 0.5115
Pump Eff. | (%) | 0 | 44.1204 | 59.318 | 62.4649 | 51.1106 | 8.2026
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 1.04 | 1.27 | 1.51 | 1.62 | 1.66 | 1.56
Motor Input | (㎾) | 0.392 | 0.599 | 0.788 | 0.874 | 0.903 | 0.825
Motor Eff. | (%) | 62 | 62 | 62 | 62 | 62 | 62
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 80 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 0.37 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 24 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 40 | 1
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 1.8 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 62 | Maker | SUMOTO | Turbin | 30
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-5-4＿MS4-0533 |  | Customer |  |  |  | 0.5
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(5-5)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 30 | 60 | 80 | 120 | 158
Dis. Head | (m) | 46 | 41.5 | 37 | 33 | 19.9 | 0.8
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0080772 | 0.032309 | 0.057438 | 0.12924 | 0.22404
Total Head | (m) | 47 | 42.5081 | 38.0323 | 34.0574 | 21.0292 | 2.024
Water Power | (㎾) | 0 | 0.20786 | 0.37196 | 0.44411 | 0.41133 | 0.052127
Shaft Power | (㎾) | 0.31878 | 0.48378 | 0.6303 | 0.70026 | 0.72996 | 0.65736
Pump Eff. | (%) | 0 | 42.9667 | 59.0125 | 63.4206 | 56.3499 | 7.9298
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 1.57 | 1.78 | 2.02 | 2.15 | 2.2 | 2.06
Motor Input | (㎾) | 0.483 | 0.733 | 0.955 | 1.061 | 1.106 | 0.996
Motor Eff. | (%) | 66 | 66 | 66 | 66 | 66 | 66
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 80 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 0.55 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 31 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 40 | 1
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 2.5 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 66 | Maker | SUMOTO | Turbin | 30
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-5-5＿MS4-0733 |  | Customer |  |  |  | 0.5 |  | 2010.7.8
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(5-26)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 64 | 85 | 98 | 115 | 133 | 150 | 165
Dis. Head | (m) | 238 | 200 | 185 | 172 | 150 | 125 | 97 | 70
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.03676 | 0.064842 | 0.086193 | 0.11869 | 0.15875 | 0.20193 | 0.24434
Total Head | (m) | 239.7 | 201.7368 | 186.7648 | 173.7862 | 151.8187 | 126.8588 | 98.9019 | 71.9443
Water Power | (㎾) | 0 | 2.1045 | 2.5876 | 2.7761 | 2.8458 | 2.7502 | 2.4182 | 1.9349
Shaft Power | (㎾) | 1.7248 | 3.5882 | 4.0194 | 4.2273 | 4.2812 | 4.235 | 4.158 | 3.9578
Pump Eff. | (%) | 0 | 58.6511 | 64.3784 | 65.6698 | 66.473 | 64.9391 | 58.1566 | 48.8894
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 6.07 | 8.95 | 9.7 | 10.1 | 10.19 | 10.13 | 10 | 9.65
Motor Input | (㎾) | 2.24 | 4.66 | 5.22 | 5.49 | 5.56 | 5.5 | 5.4 | 5.14
Motor Eff. | (%) | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 80 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 4 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 172 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 40 | 1.7
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 11.2 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 77 | Maker | SUMOTO | Turbin | 31 | 28
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-5-26_MS4-5533 |  | Customer |  |  |  | 2 |  | 2010.07.10
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 11.98 | 13.62 | 14.59 | 16.52 | 18.1 | 19.43 | 21.67
380V일때의 전류치 |  | 20.6927 | 23.5255 | 25.2009 | 28.5345 | 31.2636 | 33.5609 | 37.43 | 0
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification