## Datasheet(60-1-B)3P
Submersible Motor Pump Data Sheet
1 | Model | PSS-60-1-B_MS4-3033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 8 | m | Discharge Piece | STS304
10 | Rated Capacity | 900 | ℓ/min | Impeller | STS304
11 | Shut off Head | 13 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 55 | % | Pump Shaft | STS431
14 | Min. Flow | 400 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1100 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 100 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Sumoto |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 2.2 | kW | Stator Ends | Low Carbon Steel
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 8.5 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 663 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 1 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 383 | mm | Pump | 6.9 | kg
37 | Motor | 375 | mm | Motor | 14.2 | kg
38 | Total | 758 | mm | Total | 21.1 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(60-1)
Submersible Motor Pump Data Sheet
1 | Model | PSS-60-1_MS4-5533 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 10 | m | Discharge Piece | STS304
10 | Rated Capacity | 1000 | ℓ/min | Impeller | STS304
11 | Shut off Head | 19 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 50 | % | Pump Shaft | STS431
14 | Min. Flow | 550 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1300 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 100 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Sumoto |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 4 | kW | Stator Ends | Low Carbon Steel
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 11.2 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 663 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 1 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 383 | mm | Pump | 6.9 | kg
37 | Motor | 555 | mm | Motor | 23.4 | kg
38 | Total | 938 | mm | Total | 30.3 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(60-2-BB)
Submersible Motor Pump Data Sheet
1 | Model | PSS-60-2-BB_MS4-5533 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 12 | m | Discharge Piece | STS304
10 | Rated Capacity | 1000 | ℓ/min | Impeller | STS304
11 | Shut off Head | 26 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 550 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1300 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 100 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Sumoto |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 4 | kW | Stator Ends | Low Carbon Steel
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 11.2 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 663 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 2 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 496 | mm | Pump | 9.2 | kg
37 | Motor | 555 | mm | Motor | 23.4 | kg
38 | Total | 1051 | mm | Total | 32.6 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(60-2)
Submersible Motor Pump Data Sheet
1 | Model | PSS-60-2_MS4-7533 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 21 | m | Discharge Piece | STS304
10 | Rated Capacity | 1000 | ℓ/min | Impeller | STS304
11 | Shut off Head | 39 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 550 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1300 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 100 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 5.5 | kw | Stator Ends | Low Carbon Steel
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 15.6 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 663 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 2 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 496 | mm | Pump | 9.2 | kg
37 | Motor | 675 | mm | Motor | 29.4 | kg
38 | Total | 1171 | mm | Total | 38.6 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(60-3-A)
Submersible Motor Pump Data Sheet
1 | Model | PSS-60-3-A_MS6-10033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 35 | m | Discharge Piece | STS304
10 | Rated Capacity | 1000 | ℓ/min | Impeller | STS304
11 | Shut off Head | 53 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 550 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1400 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 100 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Sumoto |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 7.5 | kW | Stator Ends | Low Carbon Steel
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 19.2 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 1020 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 3 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 609 | mm | Pump | 11.5 | kg
37 | Motor | 600 | mm | Motor | 42 | kg
38 | Total | 1209 | mm | Total | 53.5 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(60-4)
Submersible Motor Pump Data Sheet
1 | Model | PSS-60-4_MS6-15033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 48 | m | Discharge Piece | STS304
10 | Rated Capacity | 1000 | ℓ/min | Impeller | STS304
11 | Shut off Head | 77 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 550 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1400 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 100 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Sumoto |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 11 | kW | Stator Ends | Low Carbon Steel
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 29.4 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 1020 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 4 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 722 | mm | Pump | 13.7 | kg
37 | Motor | 700 | mm | Motor | 48 | kg
38 | Total | 1422 | mm | Total | 61.7 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(60-6-B)
Submersible Motor Pump Data Sheet
1 | Model | PSS-60-6-B_MS6-20033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 70 | m | Discharge Piece | STS304
10 | Rated Capacity | 1000 | ℓ/min | Impeller | STS304
11 | Shut off Head | 105 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 65 | % | Pump Shaft | STS431
14 | Min. Flow | 550 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1400 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 100 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Sumoto |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 15 | kW | Stator Ends | Low Carbon Steel
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 38 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 1020 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 6 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 948 | mm | Pump | 18.3 | kg
37 | Motor | 760 | mm | Motor | 54 | kg
38 | Total | 1708 | mm | Total | 72.3 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(60-7)
Submersible Motor Pump Data Sheet
1 | Model | PSS-60-7_MS6-25033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 80 | m | Discharge Piece | STS304
10 | Rated Capacity | 1000 | ℓ/min | Impeller | STS304
11 | Shut off Head | 135 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 65 | % | Pump Shaft | STS431
14 | Min. Flow | 550 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1400 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 100 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Sumoto |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 18.5 | kW | Stator Ends | Low Carbon Steel
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 45.6 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 1020 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 7 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1061 | mm | Pump | 20.6 | kg
37 | Motor | 830 | mm | Motor | 65 | kg
38 | Total | 1891 | mm | Total | 85.6 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(60-9-B)
Submersible Motor Pump Data Sheet
1 | Model | PSS-60-9-B_MS6-30033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 110 | m | Discharge Piece | STS304
10 | Rated Capacity | 1000 | ℓ/min | Impeller | STS304
11 | Shut off Head | 165 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 65 | % | Pump Shaft | STS431
14 | Min. Flow | 550 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1400 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 100 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Sumoto |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 22 | kW | Stator Ends | Low Carbon Steel
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 54.6 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 1020 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 9 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1287 | mm | Pump | 25.1 | kg
37 | Motor | 890 | mm | Motor | 70 | kg
38 | Total | 2177 | mm | Total | 95.1 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(60-11)
Submersible Motor Pump Data Sheet
1 | Model | PSS-60-11_MS6-40033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 120 | m | Discharge Piece | STS304
10 | Rated Capacity | 1000 | ℓ/min | Impeller | STS304
11 | Shut off Head | 225 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 65 | % | Pump Shaft | STS431
14 | Min. Flow | 550 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1400 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 100 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Sumoto |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 30 | kW | Stator Ends | Low Carbon Steel
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 75 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 2040 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 11 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1513 | mm | Pump | 29.7 | kg
37 | Motor | 1030 | mm | Motor | 90 | kg
38 | Total | 2543 | mm | Total | 119.7 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
DIEMENSION(mm)
MODEL | MOTOR | P.L |  |  | M.L |  |  | T.L
PSS-60-1-B | MS4-3033 | 383 |  |  | 375 |  |  | 758
PSS-60-1 | MS4-5533 | 383 |  |  | 555 |  |  | 938
PSS-60-2-BB | MS4-5533 | 496 |  |  | 555 |  |  | 1051
PSS-60-2 | MS4-7533 | 496 |  |  | 675 |  |  | 1171
PSS-60-3-A | MS6-10033 | 609 |  |  | 600 |  |  | 1209
PSS-60-4 | MS6-15033 | 722 |  |  | 700 |  |  | 1422
PSS-60-6-B | MS6-20033 | 948 |  |  | 760 |  |  | 1708
PSS-60-6 | MS6-25033 | 948 |  |  | 830 |  |  | 1778
PSS-60-7 | MS6-25033 | 1061 |  |  | 830 |  |  | 1891
PSS-60-8 | MS6-30033 | 1174 |  |  | 890 |  |  | 2064
PSS-60-9-B | MS6-30033 | 1287 |  |  | 890 |  |  | 2177
PSS-60-11 | MS6-40033 | 1513 |  |  | 1030 |  |  | 2543
WEIGHT(kg)
MODEL | MOTOR | PUMP |  |  | MOTOR |  |  | TOTAL
PSS-60-1-B | MS4-3033 | 6.9 |  |  | 14.2 |  |  | 21.1
PSS-60-1 | MS4-5533 | 6.9 |  |  | 23.4 |  |  | 30.3
PSS-60-2-BB | MS4-5533 | 9.2 |  |  | 23.4 |  |  | 32.6
PSS-60-2 | MS4-7533 | 9.2 |  |  | 29.4 |  |  | 38.6
PSS-60-3-A | MS6-10033 | 11.5 |  |  | 42 |  |  | 53.5
PSS-60-4 | MS6-15033 | 13.7 |  |  | 48 |  |  | 61.7
PSS-60-6-B | MS6-20033 | 18.3 |  |  | 54 |  |  | 72.3
PSS-60-6 | MS6-25033 | 18.3 |  |  | 65 |  |  | 83.3
PSS-60-7 | MS6-25033 | 20.6 |  |  | 65 |  |  | 85.6
PSS-60-8 | MS6-30033 | 22.9 |  |  | 70 |  |  | 92.9
PSS-60-9-B | MS6-30033 | 25.1 |  |  | 70 |  |  | 95.1
PSS-60-11 | MS6-40033 | 29.7 |  |  | 90 |  |  | 119.7
※MOTOR MAKER : SUMOTO
※DISCHARGE CONNECTION : 4" (100mm)
|  |  | TYPE |  |  | SUBMERSIBLE PUMP
MODEL
SERVICE
|  |  | SCALE:N/S |  |  |  | 3rd. ANGLE PROJECT
145mm
P.L
M.L
T.L
Cable Guard Included
Outline Drawing
of PSS-60 Series

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO | 품 명 |  |  | 재 질 |  | 수량
1 | Discharge |  |  | STS304 |  | 1
2 | Valve Cone |  |  |  |  | 1
3 | Valve Seat |  |  | NBR |  | Stages
4 | Top Diffuser |  |  | STS304 |  | 1
5 | Upper Bearing |  |  |  |  | 1
6 | Neck Ring |  |  | NBR |  | 1
7 | Bearing |  |  |  |  | 1
8 | Diffuser |  |  | STS304 |  | Stages
9 | Split Cone Nut |  |  |  |  | Stages
10 | Split Cone |  |  |  |  | Stages
11 | Impeller Ring |  |  |  |  | Stages
12 | Impeller |  |  |  |  | Stages
13 | Buttom Diffuser |  |  |  |  | 1
14 | Lower Bearing |  |  | - |  | 1
15 | Stop Ring |  |  | - |  | 1
16 | Space Washer |  |  | STS304 |  | 1
17 | Nut for Stop Ring |  |  |  |  | 1
18 | Buttom Neck Ring |  |  | NBR |  | 1
19 | Strainer |  |  | STS304 |  | 1
20 | Suction Interconnector |  |  |  |  | 1
21 | Pump Shaft |  |  | STS431 |  | 1
22 | Coupling |  |  | STS304 |  | 1
23 | Strap |  |  |  |  | 4
24 | Nut |  |  |  |  | 4
|  | TYPE |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
Sectional Drawing
of PSS-60 Series

## Test Report(60-1-B)3P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 300 | 500 | 650 | 750 | 900 | 1000 | 1200
Dis. Head | (m) | 13 | 11.6 | 10.3 | 8.5 | 7.5 | 6.3 | 5 | 2.2
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.020678 | 0.057438 | 0.09707 | 0.12924 | 0.1861 | 0.22975 | 0.33084
Total Head | (m) | 14.7 | 13.3207 | 12.0574 | 10.2971 | 9.3292 | 8.1861 | 6.9298 | 4.2308
Water Power | (㎾) | 0 | 0.65138 | 0.98268 | 1.091 | 1.1405 | 1.2009 | 1.1295 | 0.82755
Shaft Power | (㎾) | 1.53 | 1.7325 | 1.8525 | 1.935 | 1.995 | 2.1 | 2.1525 | 2.1375
Pump Eff. | (%) | 0 | 37.5978 | 53.0462 | 56.3811 | 57.1679 | 57.1857 | 52.4762 | 38.7159
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 5.16 | 5.43 | 5.6 | 5.7 | 5.79 | 5.97 | 6.05 | 6.03
Motor Input | (㎾) | 2.04 | 2.31 | 2.47 | 2.58 | 2.66 | 2.8 | 2.87 | 2.85
Motor Eff. | (%) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 900 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 8 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 100 | 1.7
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 6.85 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 75 | Maker | SUMOTO | Turbin | 31 | 28
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-60-1-B_MS4-3033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 11.98 | 13.62 | 14.59 | 16.52 | 18.1 | 19.43 | 21.67
440V일때의 전류치 |  | 20.6927 | 23.5255 | 25.2009 | 28.5345 | 31.2636 | 33.5609 | 37.43 | 0
|  | 0 | 75 | 167 | 210 | 278 | 363 | 405
|  | 0 | 1.019 | 2.269 | 2.8533 | 3.7772 | 4.9321 | 5.5027
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(60-1)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 300 | 500 | 650 | 800 | 1000 | 1250 | 1400
Dis. Head | (m) | 20 | 19 | 17 | 14.8 | 12.1 | 10 | 7 | 4.5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.020678 | 0.057438 | 0.09707 | 0.14704 | 0.22975 | 0.35899 | 0.45031
Total Head | (m) | 21.7 | 20.7207 | 18.7574 | 16.5971 | 13.947 | 11.9298 | 9.059 | 6.6503
Water Power | (㎾) | 0 | 1.0132 | 1.5287 | 1.7585 | 1.8187 | 1.9445 | 1.8458 | 1.5176
Shaft Power | (㎾) | 2.8413 | 3.1262 | 3.157 | 3.1416 | 3.1647 | 3.3341 | 3.5266 | 3.5805
Pump Eff. | (%) | 0 | 32.4113 | 48.4235 | 55.9734 | 57.4681 | 58.3231 | 52.3385 | 42.3852
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 7.7 | 8.16 | 8.24 | 8.24 | 8.24 | 8.53 | 8.85 | 8.96
Motor Input | (㎾) | 3.69 | 4.06 | 4.1 | 4.08 | 4.11 | 4.33 | 4.58 | 4.65
Motor Eff. | (%) | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 1000 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 4 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 10 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 100 | 1.7
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 11.2 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 77 | Maker | SUMOTO | Turbin | 31
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-60-1_MS4-5533 |  | Customer
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 11.98 | 13.62 | 14.59 | 16.52 | 18.1 | 19.43 | 21.67
440V일때의 전류치 |  | 20.6927 | 23.5255 | 25.2009 | 28.5345 | 31.2636 | 33.5609 | 37.43 | 0
|  | 0 | 75 | 167 | 210 | 278 | 363 | 405
|  | 0 | 1.019 | 2.269 | 2.8533 | 3.7772 | 4.9321 | 5.5027
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(60-2-BB)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 300 | 500 | 650 | 800 | 1000 | 1200 | 1300
Dis. Head | (m) | 27.3 | 25.2 | 22.8 | 20 | 17.3 | 14 | 9 | 5.5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.020678 | 0.057438 | 0.09707 | 0.14704 | 0.22975 | 0.33084 | 0.38828
Total Head | (m) | 29 | 26.9207 | 24.5574 | 21.7971 | 19.147 | 15.9298 | 11.0308 | 7.5883
Water Power | (㎾) | 0 | 1.3164 | 2.0014 | 2.3094 | 2.4968 | 2.5965 | 2.1576 | 1.608
Shaft Power | (㎾) | 2.9953 | 3.465 | 3.696 | 3.8577 | 3.9963 | 4.0964 | 4.0194 | 3.9424
Pump Eff. | (%) | 0 | 37.992 | 54.1513 | 59.8647 | 62.4771 | 63.3861 | 53.6805 | 40.7862
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 7.95 | 8.77 | 9.17 | 9.44 | 9.7 | 9.9 | 9.73 | 9.58
Motor Input | (㎾) | 3.89 | 4.5 | 4.8 | 5.01 | 5.19 | 5.32 | 5.22 | 5.12
Motor Eff. | (%) | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 1000 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 4 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 12 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 100 | 1.7
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 11.2 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 77 | Maker | SUMOTO | Turbin | 31
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-60-2-BB_MS4-5533 |  | Customer
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 11.98 | 13.62 | 14.59 | 16.52 | 18.1 | 19.43 | 21.67
440V일때의 전류치 |  | 20.6927 | 23.5255 | 25.2009 | 28.5345 | 31.2636 | 33.5609 | 37.43 | 0
|  | 0 | 75 | 167 | 210 | 278 | 363 | 405
|  | 0 | 1.019 | 2.269 | 2.8533 | 3.7772 | 4.9321 | 5.5027
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(60-2)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 300 | 500 | 800 | 1000 | 1200 | 1500
Dis. Head | (m) | 39.3 | 38 | 34.8 | 26.7 | 22.8 | 18.5 | 9.5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.020678 | 0.057438 | 0.14704 | 0.22975 | 0.33084 | 0.51694
Total Head | (m) | 41 | 39.7207 | 36.5574 | 28.547 | 24.7298 | 20.5308 | 11.7169
Water Power | (㎾) | 0 | 1.9423 | 2.9794 | 3.7225 | 4.0309 | 4.0158 | 2.8648
Shaft Power | (㎾) | 4.9998 | 5.6628 | 5.7642 | 5.7642 | 5.9358 | 6.0606 | 6.0138
Pump Eff. | (%) | 0 | 34.3 | 51.6885 | 64.5802 | 67.9091 | 66.2613 | 47.637
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 12.27 | 13.47 | 13.64 | 13.65 | 13.93 | 14.2 | 14.1
Motor Input | (㎾) | 6.41 | 7.26 | 7.39 | 7.39 | 7.61 | 7.77 | 7.71
Motor Eff. | (%) | 78 | 78 | 78 | 78 | 78 | 78 | 78
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 1000 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 5.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 21 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 100 | 1.7
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 15.6 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 78 | Maker | SUMOTO | Turbin | 31 | 28
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-60-2_MS4-7533 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(60-3-A)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 308 | 606 | 911 | 1285 | 1408 | 1692
Dis. Head | (m) | 54.5 | 52 | 44.5 | 36 | 25 | 17 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.021795 | 0.084373 | 0.19068 | 0.37937 | 0.45547 | 0.65775
Total Head | (m) | 57 | 54.5218 | 47.0844 | 38.6907 | 27.8794 | 19.9555 | 3.1577
Water Power | (㎾) | 0 | 2.7372 | 4.6509 | 5.7453 | 5.8395 | 4.5799 | 0.87089
Shaft Power | (㎾) | 7.0224 | 8.048 | 8.296 | 8.456 | 8.696 | 8.616 | 7.872
Pump Eff. | (%) | 0 | 34.0111 | 56.062 | 67.9434 | 67.1513 | 53.1553 | 11.0632
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 15.56 | 17.37 | 17.83 | 18.12 | 18.64 | 18.45 | 17.06
Motor Input | (㎾) | 8.778 | 10.06 | 10.37 | 10.57 | 10.87 | 10.77 | 9.84
Motor Eff. | (%) | 80 | 80 | 80 | 80 | 80 | 80 | 80
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 1000 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 7.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 35 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 100 | 2.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 19.2 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 80 | Maker | SUMOTO | Turbin | 12
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-60-3-A_MS6-10033 |  | Customer
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(60-4)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 308 | 616 | 900 | 1232 | 1504 | 1742
Dis. Head | (m) | 79 | 78 | 65 | 50 | 38 | 21 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.021795 | 0.087181 | 0.1861 | 0.34872 | 0.5197 | 0.6972
Total Head | (m) | 81.5 | 80.5218 | 67.5872 | 52.6861 | 40.8487 | 24.0197 | 3.1972
Water Power | (㎾) | 0 | 4.0425 | 6.7863 | 7.7291 | 8.2031 | 5.8885 | 0.90783
Shaft Power | (㎾) | 9.4284 | 10.9269 | 11.2914 | 11.5668 | 11.8665 | 11.502 | 10.4409
Pump Eff. | (%) | 0 | 36.996 | 60.1014 | 66.821 | 69.128 | 51.1953 | 8.695
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 23.03 | 25.54 | 26.18 | 26.73 | 27.19 | 26.53 | 24.65
Motor Input | (㎾) | 11.64 | 13.49 | 13.94 | 14.28 | 14.65 | 14.2 | 12.89
Motor Eff. | (%) | 81 | 81 | 81 | 81 | 81 | 81 | 81
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 1000 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 11 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 48 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 100 | 2.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 29.4 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 81 | Maker | SUMOTO | Turbin | 16
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-60-4_MS6-15033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(60-6-B)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 360 | 615 | 1044 | 1220 | 1510 | 1754
Dis. Head | (m) | 110 | 102 | 93 | 75 | 60 | 38 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.029776 | 0.086898 | 0.25041 | 0.34196 | 0.52386 | 0.70684
Total Head | (m) | 112.5 | 104.5298 | 95.5869 | 77.7504 | 62.842 | 41.0239 | 3.2068
Water Power | (㎾) | 0 | 6.1338 | 9.5821 | 13.2309 | 12.4968 | 10.0972 | 0.91684
Shaft Power | (㎾) | 11.7777 | 14.1598 | 15.853 | 17.7703 | 17.6043 | 16.6747 | 15.1475
Pump Eff. | (%) | 0 | 43.3185 | 60.4435 | 74.4554 | 70.9869 | 60.554 | 6.0528
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 27.56 | 31.57 | 32.49 | 35.5 | 35.9 | 34.8 | 33.17
Motor Input | (㎾) | 14.19 | 17.06 | 19.1 | 21.41 | 21.21 | 20.09 | 18.25
Motor Eff. | (%) | 83 | 83 | 83 | 83 | 83 | 83 | 83
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 1000 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 15 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 70 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 100 | 2.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 38 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 83 | Maker | SUMOTO | Turbin | 16 | 16
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-60-6-B_MS6-20033 |  | Customer
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(60-7)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 360 | 615 | 1044 | 1220 | 1510 | 1754
Dis. Head | (m) | 138 | 135 | 117 | 83 | 69 | 40 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.029776 | 0.086898 | 0.25041 | 0.34196 | 0.52386 | 0.70684
Total Head | (m) | 140.5 | 137.5298 | 119.5869 | 85.7504 | 71.842 | 43.0239 | 3.2068
Water Power | (㎾) | 0 | 8.0702 | 11.988 | 14.5923 | 14.2865 | 10.5895 | 0.91684
Shaft Power | (㎾) | 16.7328 | 19.5552 | 19.866 | 20.3952 | 20.2692 | 19.3704 | 16.8672
Pump Eff. | (%) | 0 | 41.2691 | 60.3442 | 71.5478 | 70.4838 | 54.6683 | 5.4356
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 37.73 | 42.67 | 43.15 | 43.3 | 42.8 | 42.17 | 37.7
Motor Input | (㎾) | 19.92 | 23.28 | 23.65 | 24.28 | 24.13 | 23.06 | 20.08
Motor Eff. | (%) | 84 | 84 | 84 | 84 | 84 | 84 | 84
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 1000 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 18.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 80 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 100 | 2.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 45.6 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 84 | Maker | SUMOTO | Turbin | 15.5
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-60-7_MS6-25033 |  | Customer
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(60-9-B)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 522 | 1005 | 1257 | 1509 | 1768
Dis. Head | (m) | 170 | 160 | 112 | 87 | 55 | 1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.15284 | 0.56654 | 0.88628 | 1.2773 | 1.7533
Total Head | (m) | 172.5 | 162.6528 | 115.0665 | 90.3863 | 58.7773 | 5.2533
Water Power | (㎾) | 0 | 13.8395 | 18.8496 | 18.5193 | 14.4573 | 1.5139
Shaft Power | (㎾) | 22.95 | 26.86 | 27.285 | 27.115 | 25.755 | 22.61
Pump Eff. | (%) | 0 | 51.5245 | 69.0842 | 68.2992 | 56.1338 | 6.6958
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 47 | 53 | 53.5 | 53.6 | 53 | 46
Motor Input | (㎾) | 27 | 31.6 | 32.1 | 31.9 | 30.3 | 26.6
Motor Eff. | (%) | 85 | 85 | 85 | 85 | 85 | 85
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 1000 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 22 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 110 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 80 | 2.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 54.6 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 85 | Maker | SUMOTO | Turbin | 14 | 14
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-60-9-B_MS6-30033 |  | Customer
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(60-11)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 478 | 688 | 890 | 1100 | 1325 | 1640
Dis. Head | (m) | 227 | 200 | 170 | 150 | 120 | 80 | 10
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.052495 | 0.10875 | 0.18199 | 0.278 | 0.40336 | 0.61794
Total Head | (m) | 228.5 | 201.5525 | 171.6088 | 151.682 | 121.778 | 81.9034 | 12.1179
Water Power | (㎾) | 0 | 15.7038 | 19.2449 | 22.0045 | 21.8348 | 17.6891 | 3.2394
Shaft Power | (㎾) | 26.095 | 31.025 | 31.28 | 31.45 | 31.62 | 30.345 | 25.33
Pump Eff. | (%) | 0 | 50.6165 | 61.5246 | 69.9666 | 69.0537 | 58.2932 | 12.7887
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 58.5 | 64.8 | 65 | 65.6 | 65.3 | 65.1 | 56.9
Motor Input | (㎾) | 30.7 | 36.5 | 36.8 | 37 | 37.2 | 35.7 | 29.8
Motor Eff. | (%) | 85 | 85 | 85 | 85 | 85 | 85 | 85
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 1000 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 30 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 120 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 100 | 1.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 75 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 85 | Maker | SUMOTO | Turbin | 19.5 | 19.5
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-60-11_MS6-40033 |  | Customer
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification