## Datasheet(77-1)
Submersible Motor Pump Data Sheet
1 | Model | PSS-77-1_MS6-7533 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 18 | m | Discharge Piece | STS304
10 | Rated Capacity | 1200 | ℓ/min | Impeller | STS304
11 | Shut off Head | 28 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 65 | % | Pump Shaft | STS431
14 | Min. Flow | 600 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1900 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 125 | mm | Strainer | STS304
17 | Out Dia. | 178mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Sumoto |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 5.5 | kW | Stator Ends | Low Carbon Steel
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 15.1 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 1020 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 1 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 618 | mm | Pump | 25.1 | kg
37 | Motor | 570 | mm | Motor | 40 | kg
38 | Total | 1188 | mm | Total | 65.1 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(77-2-BA)
Submersible Motor Pump Data Sheet
1 | Model | PSS-77-2-BA_MS6-10033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 32 | m | Discharge Piece | STS304
10 | Rated Capacity | 1200 | ℓ/min | Impeller | STS304
11 | Shut off Head | 48 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 70 | % | Pump Shaft | STS431
14 | Min. Flow | 600 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1900 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 125 | mm | Strainer | STS304
17 | Out Dia. | 178mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Sumoto |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 7.5 | kW | Stator Ends | Low Carbon Steel
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 19.2 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 1020 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 2 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 746 | mm | Pump | 28.7 | kg
37 | Motor | 600 | mm | Motor | 42 | kg
38 | Total | 1346 | mm | Total | 70.7 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(77-2)
Submersible Motor Pump Data Sheet
1 | Model | PSS-77-2_MS6-15033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 38 | m | Discharge Piece | STS304
10 | Rated Capacity | 1200 | ℓ/min | Impeller | STS304
11 | Shut off Head | 56 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 70 | % | Pump Shaft | STS431
14 | Min. Flow | 700 | ℓ/min | Coupling | STS304
15 | Max. Flow | 2000 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 125 | mm | Strainer | STS304
17 | Out Dia. | 178mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Sumoto |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 11 | kW | Stator Ends | Low Carbon Steel
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 29.4 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 1020 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 2 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 746 | mm | Pump | 28.7 | kg
37 | Motor | 700 | mm | Motor | 48 | kg
38 | Total | 1446 | mm | Total | 76.7 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(77-3-A)
Submersible Motor Pump Data Sheet
1 | Model | PSS-77-3-A_MS6-20033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 40 | m | Discharge Piece | STS304
10 | Rated Capacity | 1500 | ℓ/min | Impeller | STS304
11 | Shut off Head | 77 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 70 | % | Pump Shaft | STS431
14 | Min. Flow | 700 | ℓ/min | Coupling | STS304
15 | Max. Flow | 2000 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 125 | mm | Strainer | STS304
17 | Out Dia. | 178mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Sumoto |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 15 | kW | Stator Ends | Low Carbon Steel
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 38 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 1020 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 3 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 874 | mm | Pump | 32.3 | kg
37 | Motor | 760 | mm | Motor | 54 | kg
38 | Total | 1634 | mm | Total | 86.3 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## DataSheet(77-4-B)
Submersible Motor Pump Data Sheet
1 | Model | PSS-77-4-B_MS6-25033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 72 | m | Discharge Piece | STS304
10 | Rated Capacity | 1200 | ℓ/min | Impeller | STS304
11 | Shut off Head | 104 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 70 | % | Pump Shaft | STS431
14 | Min. Flow | 700 | ℓ/min | Coupling | STS304
15 | Max. Flow | 2000 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 125 | mm | Strainer | STS304
17 | Out Dia. | 178mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Sumoto |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 18.5 | kW | Stator Ends | Low Carbon Steel
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 45.6 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 1020 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 4 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1003 | mm | Pump | 35.9 | kg
37 | Motor | 830 | mm | Motor | 65 | kg
38 | Total | 1833 | mm | Total | 100.9 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## DataSheet(77-4)
Submersible Motor Pump Data Sheet
1 | Model | PSS-77-4_MS6-30033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 80 | m | Discharge Piece | STS304
10 | Rated Capacity | 1200 | ℓ/min | Impeller | STS304
11 | Shut off Head | 113 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 70 | % | Pump Shaft | STS431
14 | Min. Flow | 700 | ℓ/min | Coupling | STS304
15 | Max. Flow | 2000 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 125 | mm | Strainer | STS304
17 | Out Dia. | 178mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Sumoto |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 22 | kW | Stator Ends | Low Carbon Steel
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 54.6 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 1020 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 4 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1003 | mm | Pump | 35.9 | kg
37 | Motor | 890 | mm | Motor | 70 | kg
38 | Total | 1893 | mm | Total | 105.9 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## DataSheet(77-6-B)
Submersible Motor Pump Data Sheet
1 | Model | PSS-77-6-B_MS6-40033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 110 | m | Discharge Piece | STS304
10 | Rated Capacity | 1200 | ℓ/min | Impeller | STS304
11 | Shut off Head | 160 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 70 | % | Pump Shaft | STS431
14 | Min. Flow | 700 | ℓ/min | Coupling | STS304
15 | Max. Flow | 2000 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 125 | mm | Strainer | STS304
17 | Out Dia. | 178mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Sumoto |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 30 | kW | Stator Ends | Low Carbon Steel
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 75 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 2040 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 6 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1259 | mm | Pump | 43 | kg
37 | Motor | 1030 | mm | Motor | 90 | kg
38 | Total | 2289 | mm | Total | 133 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
DIEMENSION(mm)
MODEL | MOTOR | P.L |  |  | M.L |  |  | T.L
PSS-77-1 | MS6-7533 | 618 |  |  | 570 |  |  | 1188
PSS-77-2-BA | MS6-10033 | 746 |  |  | 600 |  |  | 1346
PSS-77-2 | MS6-15033 | 746 |  |  | 700 |  |  | 1446
PSS-77-3-A | MS6-20033 | 874 |  |  | 760 |  |  | 1634
PSS-77-3 | MS6-25033 | 874 |  |  | 830 |  |  | 1704
PSS-77-4-B | MS6-25033 | 1003 |  |  | 830 |  |  | 1833
PSS-77-4 | MS6-30033 | 1003 |  |  | 890 |  |  | 1893
PSS-77-5-BB | MS6-30033 | 1131 |  |  | 890 |  |  | 2021
PSS-77-6-B | MS6-40033 | 1259 |  |  | 1030 |  |  | 2289
WEIGHT(kg)
MODEL | MOTOR | PUMP |  |  | MOTOR |  |  | TOTAL
PSS-77-1 | MS6-7533 | 25.1 |  |  | 40 |  |  | 65.1
PSS-77-2-BA | MS6-10033 | 28.7 |  |  | 42 |  |  | 70.7
PSS-77-2 | MS6-15033 | 28.7 |  |  | 48 |  |  | 76.7
PSS-77-3-A | MS6-20033 | 32.3 |  |  | 54 |  |  | 86.3
PSS-77-3 | MS6-25033 | 32.3 |  |  | 65 |  |  | 97.3
PSS-77-4-B | MS6-25033 | 35.9 |  |  | 65 |  |  | 100.9
PSS-77-4 | MS6-30033 | 35.9 |  |  | 70 |  |  | 105.9
PSS-77-5-BB | MS6-30033 | 39.5 |  |  | 70 |  |  | 109.5
PSS-77-6-B | MS6-40033 | 43 |  |  | 90 |  |  | 133
※MOTOR MAKER : SUMOTO
※DISCHARGE CONNECTION : 5" (125mm)
|  |  | TYPE |  |  | SUBMERSIBLE PUMP
MODEL
SERVICE
|  |  | SCALE:N/S |  |  |  | 3rd. ANGLE PROJECT
Outline Drawing
of PSS-77 Series
P.L
M.L
T.L

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO | PART NAME |  |  |  | MATERIAL | Q'TY
1 | Discharge |  |  |  | STS304 | 1
2 | Spring |  |  |  |  | 1
3 | Upper Retainer |  |  |  |  | 1
4 | Lower Retainer |  |  |  |  | 1
5 | O-ring |  |  |  | NBR | 1
6 | Diffuser |  |  |  | STS304 | Stages
7 | Neck Ring |  |  |  | STS304+NBR | Stages
8 | Split Cone Nut |  |  |  | STS304 | Stages
9 | Ring Of Impeller |  |  |  |  | Stages
10 | Impeller |  |  |  |  | Stages
11 | Space Washer |  |  |  | MoO2+PTFE | 1
12 | Nut for Stop Ring |  |  |  | STS304 | 1
13 | Shaft |  |  |  | STS431 | 1
14 | Screw |  |  |  | STS304 | 2
15 | Key |  |  |  |  | 2
16 | Strainer |  |  |  |  | 1
17 | Cable Guard |  |  |  |  | 1~2
18 | Valve Cup |  |  |  |  | 1
19 | Valve Seat |  |  |  |  | 1
20 | Bearing |  |  |  | NBR | Stages
21 | Spilt Cone |  |  |  | STS304 | Stages
22 | Bearing |  |  |  | NBR | 1
23 | Stop Ring |  |  |  | STS304 | 1
24 | Bottom diffuser |  |  |  |  | 1
25 | Stap |  |  |  |  | 4
26 | Coupling |  |  |  | STS304 | 1
27 | Spring Washer |  |  |  | STS304 | 4
28 | Nut |  |  |  |  | 4
29 | O-ring |  |  |  | NBR | 1
30 | Pump Base |  |  |  | STS304 | 1
| TYPE |  | SUBMERSIBEL PUMP
MODEL
SERVICE
| SCALE:N/S |  |  | 3rd. ANGLE PROJECT
Sectional Drawing
of PSS-77 Series

## Test Report(77-1)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 605 | 1007 | 1404 | 1587 | 1807 | 2179
Dis. Head | (m) | 28 | 25 | 18.5 | 15 | 12.5 | 9.5 | 2.5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.034445 | 0.095428 | 0.1855 | 0.23701 | 0.30728 | 0.44682
Total Head | (m) | 30.5 | 27.5344 | 21.0954 | 17.6855 | 15.237 | 12.3073 | 5.4468
Water Power | (㎾) | 0 | 2.7153 | 3.4626 | 4.0474 | 3.9415 | 3.625 | 1.9346
Shaft Power | (㎾) | 4.266 | 5.0007 | 5.3325 | 5.9013 | 6.083 | 6.162 | 5.9882
Pump Eff. | (%) | 0 | 54.2986 | 64.9344 | 68.5843 | 64.7958 | 58.8283 | 32.3066
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 11.31 | 12.46 | 13.05 | 14.01 | 14.41 | 14.51 | 14.3
Motor Input | (㎾) | 5.4 | 6.33 | 6.75 | 7.47 | 7.7 | 7.8 | 7.58
Motor Eff. | (%) | 79 | 79 | 79 | 79 | 79 | 79 | 79
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 1200 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 5.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 18 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 125 | 2.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 15.1 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 79 | Maker | SUMOTO | Turbin | 12
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-77-1_MS6-7533 |  | Customer
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(77-2-BA)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 408 | 807 | 1209 | 1608 | 1787 | 2153
Dis. Head | (m) | 48.5 | 46 | 39 | 31.5 | 22 | 15.5 | 2.5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.015665 | 0.061287 | 0.13755 | 0.24333 | 0.30052 | 0.43622
Total Head | (m) | 51 | 48.5157 | 41.5613 | 34.1376 | 24.7433 | 18.3005 | 5.4362
Water Power | (㎾) | 0 | 3.2265 | 5.467 | 6.7274 | 6.4853 | 5.3306 | 1.9078
Shaft Power | (㎾) | 6.824 | 7.776 | 8.504 | 9.416 | 9.648 | 9.512 | 8.592
Pump Eff. | (%) | 0 | 41.4929 | 64.2875 | 71.4463 | 67.2194 | 56.0407 | 22.2042
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 16.28 | 17.97 | 18.3 | 18.9 | 19.1 | 19.05 | 18.89
Motor Input | (㎾) | 8.53 | 9.72 | 10.63 | 11.77 | 12.06 | 11.89 | 10.74
Motor Eff. | (%) | 80 | 80 | 80 | 80 | 80 | 80 | 80
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 1200 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 7.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 32 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 125 | 2.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 19.2 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 80 | Maker | SUMOTO | Turbin | 12
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-77-2-BA_MS6-10033 |  | Customer
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(77-2)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 508 | 1013 | 1586 | 2000 | 2335
Dis. Head | (m) | 56 | 52 | 40.5 | 30.5 | 17.5 | 2.2
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.024285 | 0.096569 | 0.23671 | 0.37643 | 0.51309
Total Head | (m) | 58.5 | 54.5243 | 43.0966 | 33.2367 | 20.3764 | 5.2131
Water Power | (㎾) | 0 | 4.5148 | 7.1161 | 8.5923 | 6.6427 | 1.9841
Shaft Power | (㎾) | 8.24 | 9.576 | 10.312 | 11.552 | 11.536 | 11.264
Pump Eff. | (%) | 0 | 47.1473 | 69.0076 | 74.3792 | 57.5825 | 17.6148
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 20.91 | 23.02 | 24.32 | 26.54 | 26.46 | 26.04
Motor Input | (㎾) | 10.3 | 11.97 | 12.89 | 14.44 | 14.42 | 14.08
Motor Eff. | (%) | 80 | 80 | 80 | 80 | 80 | 80
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 1200 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 15 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 38 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 125 | 2.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 29.4 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 80 | Maker | SUMOTO | Turbin | 14 | 14
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-77-2_MS6-15033 |  | Customer
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(77-3-A)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 505 | 1013 | 1616 | 2007 | 2300
Dis. Head | (m) | 77.5 | 72.3 | 57.5 | 40.5 | 21.5 | 2.5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.023999 | 0.096569 | 0.24575 | 0.37907 | 0.49782
Total Head | (m) | 80 | 74.824 | 60.0966 | 43.2458 | 24.3791 | 5.4978
Water Power | (㎾) | 0 | 6.1591 | 9.9231 | 11.3913 | 7.9754 | 2.0611
Shaft Power | (㎾) | 11.3129 | 13.2551 | 14.5665 | 15.7783 | 15.0977 | 13.4958
Pump Eff. | (%) | 0 | 46.4662 | 68.1226 | 72.1958 | 52.8252 | 15.2724
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 26.71 | 29.89 | 32.14 | 34.36 | 33.21 | 30.4
Motor Input | (㎾) | 13.63 | 15.97 | 17.55 | 19.01 | 18.19 | 16.26
Motor Eff. | (%) | 83 | 83 | 83 | 83 | 83 | 83
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 1200 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 15 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 53 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 125 | 2.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 38 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 83 | Maker | SUMOTO | Turbin | 14 | 14
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-77-3-A_MS6-20033 |  | Customer
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(77-4-B)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 510 | 1001 | 1509 | 1795 | 2001 | 2333
Dis. Head | (m) | 104 | 98 | 79 | 61 | 45.5 | 31 | 2
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.024477 | 0.094295 | 0.21429 | 0.30321 | 0.3768 | 0.51221
Total Head | (m) | 106.5 | 100.5245 | 81.5943 | 63.7143 | 48.3032 | 33.8768 | 5.0122
Water Power | (㎾) | 0 | 8.3566 | 13.3132 | 15.6716 | 14.1328 | 11.0494 | 1.906
Shaft Power | (㎾) | 15.4056 | 18.1356 | 19.7736 | 21.4788 | 21.3276 | 20.8068 | 18.186
Pump Eff. | (%) | 0 | 46.0784 | 67.328 | 72.9632 | 66.2653 | 53.1046 | 10.4808
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 34.98 | 39.61 | 40.1 | 42.5 | 42.6 | 41.7 | 39.81
Motor Input | (㎾) | 18.34 | 21.59 | 23.54 | 25.57 | 25.39 | 24.77 | 21.65
Motor Eff. | (%) | 84 | 84 | 84 | 84 | 84 | 84 | 84
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 1200 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 18.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 72 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 125 | 2.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 45.6 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 84 | Maker | SUMOTO | Turbin | 15 | 15
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-77-4-B_MS6-25033 |  | Customer
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(77-4)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 501 | 1007 | 1508 | 1690 | 2008 | 2389
Dis. Head | (m) | 113 | 107 | 85 | 69 | 60.5 | 40 | 3
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.023621 | 0.095428 | 0.214 | 0.26878 | 0.37944 | 0.5371
Total Head | (m) | 115.5 | 109.5236 | 87.5954 | 71.714 | 63.2688 | 42.8794 | 6.0371
Water Power | (㎾) | 0 | 8.944 | 14.378 | 17.6276 | 17.4287 | 14.0346 | 2.3509
Shaft Power | (㎾) | 16.9915 | 19.9155 | 21.2755 | 23.494 | 23.715 | 23.273 | 21.93
Pump Eff. | (%) | 0 | 44.9099 | 67.5801 | 75.0302 | 73.4921 | 60.3043 | 10.72
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 38.39 | 43.17 | 45.57 | 49.48 | 49.88 | 49.18 | 46.8
Motor Input | (㎾) | 19.99 | 23.43 | 25.03 | 27.64 | 27.9 | 27.38 | 25.8
Motor Eff. | (%) | 85 | 85 | 85 | 85 | 85 | 85 | 85
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 1200 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 22 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 80 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 125 | 2.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 54.6 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 85 | Maker | SUMOTO | Turbin | 14 | 14
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-77-4_MS6-30033 |  | Customer
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(77-6)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 505 | 1009 | 1540 | 2005 | 2330
Dis. Head | (m) | 161 | 152 | 122 | 92 | 47.5 | 1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.023999 | 0.095808 | 0.22318 | 0.37831 | 0.51089
Total Head | (m) | 164 | 155.024 | 125.0958 | 95.2232 | 50.8783 | 4.5109
Water Power | (㎾) | 0 | 12.7608 | 20.5741 | 23.9029 | 16.6278 | 1.7132
Shaft Power | (㎾) | 24.565 | 28.645 | 30.94 | 33.83 | 32.385 | 28.815
Pump Eff. | (%) | 0 | 44.5481 | 66.4969 | 70.656 | 51.3441 | 5.9455
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 54 | 61 | 63 | 65 | 64 | 61
Motor Input | (㎾) | 28.9 | 33.7 | 36.4 | 39.8 | 38.1 | 33.9
Motor Eff. | (%) | 85 | 85 | 85 | 85 | 85 | 85
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 1200 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 30 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 110 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 125 | 3
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 75 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 85 | Maker | SUMOTO | Turbin | 14 | 14
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-77-6-B_MS6-40033 |  | Customer
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification