## Datasheet(77-1)
Submersible Motor Pump Data Sheet
1 | Model | PSS-77-1_MF6-7533 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 18 | m | Discharge Piece | STS304
10 | Rated Capacity | 1300 | ℓ/min | Impeller | STS304
11 | Shut off Head | 28 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 70 | % | Pump Shaft | STS431
14 | Min. Flow | 600 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1900 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 125 | mm | Strainer | STS304
17 | Out Dia. | 178mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 5.5 | kW | Stator Ends | Low Carbon Steel
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 15 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 680 kgf / 1500 lbs |  | Castings | Gray Iron
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 1 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 618 | mm | Pump | 25.1 | kg
37 | Motor | 615 | mm | Motor | 48 | kg
38 | Total | 1233 | mm | Total | 73.1 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(77-2-BA)
Submersible Motor Pump Data Sheet
1 | Model | PSS-77-2-BA_MF6-10033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 22 | m | Discharge Piece | STS304
10 | Rated Capacity | 1300 | ℓ/min | Impeller | STS304
11 | Shut off Head | 40 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 73 | % | Pump Shaft | STS431
14 | Min. Flow | 600 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1900 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 125 | mm | Strainer | STS304
17 | Out Dia. | 178mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 7.5 | kW | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 19.6 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 2 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 746 | mm | Pump | 28.7 | kg
37 | Motor | 645 | mm | Motor | 52 | kg
38 | Total | 1391 | mm | Total | 80.7 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(77-2)
Submersible Motor Pump Data Sheet
1 | Model | PSS-77-2_MF6-15033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 35 | m | Discharge Piece | STS304
10 | Rated Capacity | 1300 | ℓ/min | Impeller | STS304
11 | Shut off Head | 56 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 70 | % | Pump Shaft | STS431
14 | Min. Flow | 700 | ℓ/min | Coupling | STS304
15 | Max. Flow | 2000 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 125 | mm | Strainer | STS304
17 | Out Dia. | 178mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 11 | kW | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 28.9 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 2 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 746 | mm | Pump | 28.7 | kg
37 | Motor | 711 | mm | Motor | 58 | kg
38 | Total | 1457 | mm | Total | 86.7 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(77-3-A)
Submersible Motor Pump Data Sheet
1 | Model | PSS-77-3-A_MF6-20033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 50 | m | Discharge Piece | STS304
10 | Rated Capacity | 1300 | ℓ/min | Impeller | STS304
11 | Shut off Head | 77 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 70 | % | Pump Shaft | STS431
14 | Min. Flow | 700 | ℓ/min | Coupling | STS304
15 | Max. Flow | 2000 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 125 | mm | Strainer | STS304
17 | Out Dia. | 178mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 15 | kW | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 37.3 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 3 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 874 | mm | Pump | 32.3 | kg
37 | Motor | 777 | mm | Motor | 64 | kg
38 | Total | 1651 | mm | Total | 96.3 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## DataSheet(77-4-B)
Submersible Motor Pump Data Sheet
1 | Model | PSS-77-4-B_MF6-25033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 67 | m | Discharge Piece | STS304
10 | Rated Capacity | 1300 | ℓ/min | Impeller | STS304
11 | Shut off Head | 104 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 70 | % | Pump Shaft | STS431
14 | Min. Flow | 700 | ℓ/min | Coupling | STS304
15 | Max. Flow | 2000 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 125 | mm | Strainer | STS304
17 | Out Dia. | 178mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 18.5 | kW | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 46 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 4 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1003 | mm | Pump | 35.9 | kg
37 | Motor | 841 | mm | Motor | 70 | kg
38 | Total | 1844 | mm | Total | 105.9 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## DataSheet(77-4)
Submersible Motor Pump Data Sheet
1 | Model | PSS-77-4_MF6-30033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 75 | m | Discharge Piece | STS304
10 | Rated Capacity | 1300 | ℓ/min | Impeller | STS304
11 | Shut off Head | 113 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 72 | % | Pump Shaft | STS431
14 | Min. Flow | 700 | ℓ/min | Coupling | STS304
15 | Max. Flow | 2000 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 125 | mm | Strainer | STS304
17 | Out Dia. | 178mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 22 | kW | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 55.4 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 4 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1003 | mm | Pump | 35.9 | kg
37 | Motor | 907 | mm | Motor | 76 | kg
38 | Total | 1910 | mm | Total | 111.9 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## DataSheet(77-6-B)
Submersible Motor Pump Data Sheet
1 | Model | PSS-77-6-B_MF6-40033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 105 | m | Discharge Piece | STS304
10 | Rated Capacity | 1300 | ℓ/min | Impeller | STS304
11 | Shut off Head | 160 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 69 | % | Pump Shaft | STS431
14 | Min. Flow | 700 | ℓ/min | Coupling | STS304
15 | Max. Flow | 2000 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 125 | mm | Strainer | STS304
17 | Out Dia. | 178mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 30 | kW | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 74.6 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 6 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1259 | mm | Pump | 43 | kg
37 | Motor | 1036 | mm | Motor | 92 | kg
38 | Total | 2295 | mm | Total | 135 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## DataSheet(77-7)
Submersible Motor Pump Data Sheet
1 | Model | PSS-77-7_MF6-50033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 130 | m | Discharge Piece | STS304
10 | Rated Capacity | 1300 | ℓ/min | Impeller | STS304
11 | Shut off Head | 195 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 67 | % | Pump Shaft | STS431
14 | Min. Flow | 700 | ℓ/min | Coupling | STS304
15 | Max. Flow | 2000 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 125 | mm | Strainer | STS304
17 | Out Dia. | 178mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 37 | kW | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 95 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 7 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1387 | mm | Pump | 46.6 | kg
37 | Motor | 1405 | mm | Motor | 136 | kg
38 | Total | 2792 | mm | Total | 182.6 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
DIEMENSION(mm)
MODEL | MOTOR | P.L |  |  | M.L |  |  | T.L
PSS-77-1 | MF6-7533 | 618 |  |  | 615 |  |  | 1233
PSS-77-2-BA | MF6-10033 | 746 |  |  | 645 |  |  | 1391
PSS-77-2 | MF6-15033 | 746 |  |  | 711 |  |  | 1457
PSS-77-3-A | MF6-20033 | 874 |  |  | 777 |  |  | 1651
PSS-77-3 | MF6-25033 | 874 |  |  | 841 |  |  | 1715
PSS-77-4-B | MF6-25033 | 1003 |  |  | 841 |  |  | 1844
PSS-77-4 | MF6-30033 | 1003 |  |  | 907 |  |  | 1910
PSS-77-5-BB | MF6-30033 | 1131 |  |  | 907 |  |  | 2038
PSS-77-6-B | MF6-40033 | 1259 |  |  | 1036 |  |  | 2295
PSS-77-6 | MF6-50033 | 1259 |  |  | 1405 |  |  | 2664
PSS-77-7 | MF6-50033 | 1387 |  |  | 1405 |  |  | 2792
WEIGHT(kg)
MODEL | MOTOR | PUMP |  |  | MOTOR |  |  | TOTAL
PSS-77-1 | MF6-7533 | 25.1 |  |  | 48 |  |  | 73.1
PSS-77-2-BA | MF6-10033 | 28.7 |  |  | 52 |  |  | 80.7
PSS-77-2 | MF6-15033 | 28.7 |  |  | 58 |  |  | 86.7
PSS-77-3-A | MF6-20033 | 32.3 |  |  | 64 |  |  | 96.3
PSS-77-3 | MF6-25033 | 32.3 |  |  | 70 |  |  | 102.3
PSS-77-4-B | MF6-25033 | 35.9 |  |  | 70 |  |  | 105.9
PSS-77-4 | MF6-30033 | 35.9 |  |  | 76 |  |  | 111.9
PSS-77-5-BB | MF6-30033 | 39.5 |  |  | 76 |  |  | 115.5
PSS-77-6-B | MF6-40033 | 43 |  |  | 92 |  |  | 135
PSS-77-6 | MF6-50033 | 43 |  |  | 136 |  |  | 179
PSS-77-7 | MF6-50033 | 46.6 |  |  | 136 |  |  | 182.6
※MOTOR MAKER : FRANKLIN ELECTRIC U.S.A
※DISCHARGE CONNECTION : 5" (125mm)
|  |  | TYPE |  |  | SUBMERSIBLE PUMP
MODEL
SERVICE
|  |  | SCALE:N/S |  |  |  | 3rd. ANGLE PROJECT
Outline Drawing
of PSS-77 Series
P.L
M.L
T.L

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO | PART NAME |  |  |  | MATERIAL | Q'TY
1 | Discharge |  |  |  | STS304 | 1
2 | Spring |  |  |  |  | 1
3 | Upper Retainer |  |  |  |  | 1
4 | Lower Retainer |  |  |  |  | 1
5 | O-ring |  |  |  | NBR | 1
6 | Diffuser |  |  |  | STS304 | Stages
7 | Neck Ring |  |  |  | STS304+NBR | Stages
8 | Split Cone Nut |  |  |  | STS304 | Stages
9 | Ring Of Impeller |  |  |  |  | Stages
10 | Impeller |  |  |  |  | Stages
11 | Space Washer |  |  |  | MoO2+PTFE | 1
12 | Nut for Stop Ring |  |  |  | STS304 | 1
13 | Shaft |  |  |  | STS431 | 1
14 | Screw |  |  |  | STS304 | 2
15 | Key |  |  |  |  | 2
16 | Strainer |  |  |  |  | 1
17 | Cable Guard |  |  |  |  | 1~2
18 | Valve Cup |  |  |  |  | 1
19 | Valve Seat |  |  |  |  | 1
20 | Bearing |  |  |  | NBR | Stages
21 | Spilt Cone |  |  |  | STS304 | Stages
22 | Bearing |  |  |  | NBR | 1
23 | Stop Ring |  |  |  | STS304 | 1
24 | Bottom diffuser |  |  |  |  | 1
25 | Stap |  |  |  |  | 4
26 | Coupling |  |  |  | STS304 | 1
27 | Spring Washer |  |  |  | STS304 | 4
28 | Nut |  |  |  |  | 4
29 | O-ring |  |  |  | NBR | 1
30 | Pump Base |  |  |  | STS304 | 1
| TYPE |  | SUBMERSIBEL PUMP
MODEL
SERVICE
| SCALE:N/S |  |  | 3rd. ANGLE PROJECT
Sectional Drawing
of PSS-77 Series

## Test Report(77-1)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 605 | 1007 | 1404 | 1587 | 1807 | 2179
Dis. Head | (m) | 28 | 25 | 18.5 | 15 | 12.5 | 9.5 | 2.5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.034445 | 0.095428 | 0.1855 | 0.23701 | 0.30728 | 0.44682
Total Head | (m) | 30.5 | 27.5344 | 21.0954 | 17.6855 | 15.237 | 12.3073 | 5.4468
Water Power | (㎾) | 0 | 2.7153 | 3.4626 | 4.0474 | 3.9415 | 3.625 | 1.9346
Shaft Power | (㎾) | 3.996 | 4.6842 | 4.995 | 5.5278 | 5.698 | 5.772 | 5.6092
Pump Eff. | (%) | 0 | 57.9674 | 69.3218 | 73.2183 | 69.1738 | 62.8032 | 34.4895
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 11.31 | 12.46 | 13.05 | 14.01 | 14.41 | 14.51 | 14.3
Motor Input | (㎾) | 5.4 | 6.33 | 6.75 | 7.47 | 7.7 | 7.8 | 7.58
Motor Eff. | (%) | 74 | 74 | 74 | 74 | 74 | 74 | 74
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 1300 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 5.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 18 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 125 | 2.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 15 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 74 | Maker | FRANKLIN | Turbin | 12
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-77-1_MF6-7533 |  | Customer |  |  |  | 2 |  | 2008.02.22
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(77-2-BA)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 408 | 807 | 1209 | 1608 | 1787 | 2153
Dis. Head | (m) | 40 | 36 | 33 | 25 | 16 | 10 | 2.5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.015665 | 0.061287 | 0.13755 | 0.24333 | 0.30052 | 0.43622
Total Head | (m) | 42.5 | 38.5157 | 35.5613 | 27.6376 | 18.7433 | 12.8005 | 5.4362
Water Power | (㎾) | 0 | 2.5614 | 4.6778 | 5.4464 | 4.9127 | 3.7285 | 1.9078
Shaft Power | (㎾) | 4.797 | 6.3492 | 7.2774 | 7.9014 | 7.9326 | 7.3164 | 8.3772
Pump Eff. | (%) | 0 | 40.3428 | 64.278 | 68.9302 | 61.9305 | 50.9615 | 22.7735
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 13.34 | 15.86 | 17.52 | 18.66 | 18.69 | 17.56 | 17.4
Motor Input | (㎾) | 6.15 | 8.14 | 9.33 | 10.13 | 10.17 | 9.38 | 10.74
Motor Eff. | (%) | 78 | 78 | 78 | 78 | 78 | 78 | 78
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 1300 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 7.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 22 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 125 | 2.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 19.6 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 78 | Maker | FRANKLIN | Turbin | 12
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-77-2-BA_MF6-10033 |  | Customer |  |  |  | 2 |  | 2008.02.21
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(77-2)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 508 | 1013 | 1586 | 2000 | 2335
Dis. Head | (m) | 56 | 52 | 40.5 | 30.5 | 17.5 | 2.2
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.024285 | 0.096569 | 0.23671 | 0.37643 | 0.51309
Total Head | (m) | 58.5 | 54.5243 | 43.0966 | 33.2367 | 20.3764 | 5.2131
Water Power | (㎾) | 0 | 4.5148 | 7.1161 | 8.5923 | 6.6427 | 1.9841
Shaft Power | (㎾) | 8.2606 | 9.5999 | 10.3378 | 11.5809 | 11.5648 | 11.2922
Pump Eff. | (%) | 0 | 47.0298 | 68.8355 | 74.1937 | 57.4389 | 17.5708
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 20.91 | 23.02 | 24.32 | 26.54 | 26.46 | 26.04
Motor Input | (㎾) | 10.3 | 11.97 | 12.89 | 14.44 | 14.42 | 14.08
Motor Eff. | (%) | 80.2 | 80.2 | 80.2 | 80.2 | 80.2 | 80.2
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 1300 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 11 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 35 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 125 | 2.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 28.9 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 80.2 | Maker | FRANKLIN | Turbin | 14 | 14
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-77-2_MF6-15033 |  | Customer |  |  |  | 2 |  | 2008.02.27
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(77-3-A)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 505 | 1013 | 1616 | 2007 | 2300
Dis. Head | (m) | 77.5 | 72.3 | 57.5 | 40.5 | 21.5 | 2.5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.023999 | 0.096569 | 0.24575 | 0.37907 | 0.49782
Total Head | (m) | 80 | 74.824 | 60.0966 | 43.2458 | 24.3791 | 5.4978
Water Power | (㎾) | 0 | 6.1591 | 9.9231 | 11.3913 | 7.9754 | 2.0611
Shaft Power | (㎾) | 11.1221 | 13.0315 | 14.3208 | 15.5122 | 14.843 | 13.2682
Pump Eff. | (%) | 0 | 47.2634 | 69.2914 | 73.4345 | 53.7315 | 15.5344
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 26.71 | 29.89 | 32.14 | 34.36 | 33.21 | 30.4
Motor Input | (㎾) | 13.63 | 15.97 | 17.55 | 19.01 | 18.19 | 16.26
Motor Eff. | (%) | 81.6 | 81.6 | 81.6 | 81.6 | 81.6 | 81.6
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 1300 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 15 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 50 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 125 | 2.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 37.3 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 81.6 | Maker | FRANKLIN | Turbin | 14 | 14
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-77-3-A_MF6-20033 |  | Customer |  |  |  | 2 |  | 2008.02.28
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(77-4-B)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 510 | 1001 | 1509 | 1795 | 2001 | 2333
Dis. Head | (m) | 104 | 98 | 79 | 61 | 45.5 | 31 | 2
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.024477 | 0.094295 | 0.21429 | 0.30321 | 0.3768 | 0.51221
Total Head | (m) | 106.5 | 100.5245 | 81.5943 | 63.7143 | 48.3032 | 33.8768 | 5.0122
Water Power | (㎾) | 0 | 8.3566 | 13.3132 | 15.6716 | 14.1328 | 11.0494 | 1.906
Shaft Power | (㎾) | 15.0388 | 17.7038 | 19.3028 | 20.9674 | 20.8198 | 20.3114 | 17.753
Pump Eff. | (%) | 0 | 47.2023 | 68.9701 | 74.7428 | 67.8815 | 54.3998 | 10.7364
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 34.98 | 39.61 | 42.41 | 45.63 | 45.3 | 44.43 | 39.81
Motor Input | (㎾) | 18.34 | 21.59 | 23.54 | 25.57 | 25.39 | 24.77 | 21.65
Motor Eff. | (%) | 82 | 82 | 82 | 82 | 82 | 82 | 82
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 1300 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 18.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 67 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 125 | 2.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 46.0 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 82 | Maker | FRANKLIN | Turbin | 15 | 15
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-77-4-B_MF6-25033 |  | Customer |  |  |  | 2 |  | 2008.02.29
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(77-4)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 501 | 1007 | 1508 | 1690 | 2008 | 2389
Dis. Head | (m) | 113 | 107 | 85 | 69 | 60.5 | 40 | 3
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.023621 | 0.095428 | 0.214 | 0.26878 | 0.37944 | 0.5371
Total Head | (m) | 115.5 | 109.5236 | 87.5954 | 71.714 | 63.2688 | 42.8794 | 6.0371
Water Power | (㎾) | 0 | 8.944 | 14.378 | 17.6276 | 17.4287 | 14.0346 | 2.3509
Shaft Power | (㎾) | 16.5117 | 19.3532 | 20.6748 | 22.8306 | 23.0454 | 22.6159 | 21.3108
Pump Eff. | (%) | 0 | 46.2148 | 69.5437 | 77.2102 | 75.6275 | 62.0565 | 11.0314
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 38.39 | 43.17 | 45.57 | 49.48 | 49.88 | 49.18 | 46.8
Motor Input | (㎾) | 19.99 | 23.43 | 25.03 | 27.64 | 27.9 | 27.38 | 25.8
Motor Eff. | (%) | 82.6 | 82.6 | 82.6 | 82.6 | 82.6 | 82.6 | 82.6
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 1300 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 22 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 75 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 125 | 2.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 55.4 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 82.6 | Maker | FRANKLIN | Turbin | 14 | 14
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-77-4_MF6-30033 |  | Customer |  |  |  | 2 |  | 2008.03.03
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(77-6-B)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 505 | 1009 | 1540 | 2005 | 2330
Dis. Head | (m) | 161 | 152 | 122 | 92 | 47.5 | 1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.023999 | 0.095808 | 0.22318 | 0.37831 | 0.51089
Total Head | (m) | 164 | 155.024 | 125.0958 | 95.2232 | 50.8783 | 4.5109
Water Power | (㎾) | 0 | 12.7608 | 20.5741 | 23.9029 | 16.6278 | 1.7132
Shaft Power | (㎾) | 23.9292 | 27.9036 | 30.1392 | 32.9544 | 31.5468 | 28.0692
Pump Eff. | (%) | 0 | 45.7317 | 68.2637 | 72.5333 | 52.7083 | 6.1035
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 54 | 61 | 64 | 69 | 67 | 61
Motor Input | (㎾) | 28.9 | 33.7 | 36.4 | 39.8 | 38.1 | 33.9
Motor Eff. | (%) | 82.8 | 82.8 | 82.8 | 82.8 | 82.8 | 82.8
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 1300 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 29 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 105 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 125 | 3
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 74.6 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 82.8 | Maker | FRANKLIN | Turbin | 14 | 14
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-77-6-B_MF6-40033 |  | Customer |  |  |  | 2 |  | 2008.03.19
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(77-7)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 510 | 1008 | 1400 | 1500 | 2000 | 2270
Dis. Head | (m) | 197 | 187 | 148 | 125 | 116 | 61 | 1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.024477 | 0.095618 | 0.18445 | 0.21174 | 0.37643 | 0.48492
Total Head | (m) | 200 | 190.0245 | 151.0956 | 128.1844 | 119.2117 | 64.3764 | 4.4849
Water Power | (㎾) | 0 | 15.7967 | 24.8256 | 29.2517 | 29.1473 | 20.9867 | 1.6595
Shaft Power | (㎾) | 30.6806 | 35.8226 | 38.3079 | 41.3931 | 41.8216 | 40.3647 | 37.7937
Pump Eff. | (%) | 0 | 44.0971 | 64.8055 | 70.668 | 69.6943 | 51.9927 | 4.3909
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 64 | 73 | 77 | 84 | 85 | 82 | 77
Motor Input | (㎾) | 35.8 | 41.8 | 44.7 | 48.3 | 48.8 | 47.1 | 44.1
Motor Eff. | (%) | 85.7 | 85.7 | 85.7 | 85.7 | 85.7 | 85.7 | 85.7
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 1300 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 37 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 130 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 125 | 3
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 95 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 85.7 | Maker | FRANKLIN | Turbin | 6
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-77-7_MF6-50033 |  | Customer |  |  |  | 2 |  | 2008.03.20
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification