## Datasheet(8-4)3P
Submersible Motor Pump Data Sheet
1 | Model | PSS-8-4_MS4-1033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 24 | m | Discharge Piece | STS304
10 | Rated Capacity | 130 | ℓ/min | Impeller | STS304
11 | Shut off Head | 32 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 70 | ℓ/min | Coupling | STS304
15 | Max. Flow | 200 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 50 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 0.75 | kW | Stud | Low Carbon Steel
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 3.1 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Cover | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 153 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 4 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 370 | mm | Pump | 3.8 | kg
37 | Motor | 265 | mm | Motor | 8.3 | kg
38 | Total | 635 | mm | Total | 12.1 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
DIEMENSION(mm)
MODEL | MOTOR | P.L |  |  | M.L |  |  | T.L
PSS-8-4 | MS4-1033 | 370 |  |  | 265 |  |  | 635
WEIGHT(kg)
MODEL | MOTOR | PUMP |  |  | MOTOR |  |  | TOTAL
PSS-8-4 | MS4-1033 | 3.8 |  |  | 8.3 |  |  | 12.1
※DISCHARGE CONNECTION : 2" (50mm)
|  |  | TYPE |  |  | SUBMERSIBLE PUMP
MODEL
SERVICE
|  |  | SCALE:N/S |  |  |  | 3rd. ANGLE PROJECT
Outline Drawing
of PSS-8 Series
98mm
P.L
M.L
T.L
P.L
M.L
T.L
Cable Guard Included

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO | PART NAME |  |  | MATERIAL |  | Q'TY
1 | Discharge piece |  |  | STS304 |  | 1
2 | Valve cone |  |  |  |  | 1
3 | Valve seat |  |  | NBR |  | 1
4 | Bearing |  |  | NBR |  | 1
5 | Top intermediate chamber |  |  | - |  | 1
6 | Split cone nut |  |  | NBR |  | Stages
7 | Impeller |  |  |  |  | Stages
8 | Split cone |  |  | STS304 |  | Stages
9 | Neck ring |  |  | NBR |  | Stages
10 | Diffuser |  |  | STS304 |  | Stages
11 | Bottom diffuser |  |  |  |  | 1
12 | Strainer |  |  |  |  | 1
13 | Suction interconnector |  |  |  |  | 1
14 | Pump shaft/coupling |  |  | STS431/304 |  | 1
15 | Strap |  |  | STS304 |  | 4
16 | Nut |  |  |  |  | 4
17 | Cable guard |  |  |  |  | 1
|  | TYPE |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
Sectional Drawing
of PSS-8 Series

## Test Report(8-4)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 50 | 100 | 130 | 180 | 230 | 270
Dis. Head | (m) | 32 | 29.9 | 27.5 | 25.6 | 20 | 10.4 | 1.5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0091901 | 0.03676 | 0.062125 | 0.1191 | 0.19446 | 0.26798
Total Head | (m) | 33 | 30.9092 | 28.5368 | 26.6621 | 21.1191 | 11.5945 | 2.768
Water Power | (㎾) | 0 | 0.25191 | 0.46515 | 0.56497 | 0.61963 | 0.43468 | 0.12182
Shaft Power | (㎾) | 0.43608 | 0.66723 | 0.85974 | 0.95496 | 0.99912 | 0.94599 | 0.87768
Pump Eff. | (%) | 0 | 37.7546 | 54.1035 | 59.1617 | 62.018 | 45.9494 | 13.8797
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 2.05 | 2.34 | 2.65 | 2.81 | 2.89 | 2.8 | 2.67
Motor Input | (㎾) | 0.632 | 0.967 | 1.246 | 1.384 | 1.448 | 1.371 | 1.272
Motor Eff. | (%) | 69 | 69 | 69 | 69 | 69 | 69 | 69
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 130 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 0.75 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 24 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50 | 1
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 3.1 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 69 | Maker | SUMOTO | Turbin | 30
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-8-4＿MS4-1033 |  | Customer |  |  |  | 0.5
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification