## Datasheet(95-1-A)
Submersible Motor Pump Data Sheet
1 | Model | PSS-95-1-A_MF6-7533 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 11 | m | Discharge Piece | STS304
10 | Rated Capacity | 1600 | ℓ/min | Impeller | STS304
11 | Shut off Head | 22 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 65 | % | Pump Shaft | STS431
14 | Min. Flow | 700 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1800 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 125 | mm | Strainer | STS304
17 | Out Dia. | 178mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 5.5 | kW | Stator Ends | Low Carbon Steel
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 15 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 680 kgf / 1500 lbs |  | Castings | Gray Iron
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 1 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 618 | mm | Pump | 25.1 | kg
37 | Motor | 615 | mm | Motor | 48 | kg
38 | Total | 1233 | mm | Total | 73.1 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(95-1)
Submersible Motor Pump Data Sheet
1 | Model | PSS-95-1_MF6-10033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 17 | m | Discharge Piece | STS304
10 | Rated Capacity | 1600 | ℓ/min | Impeller | STS304
11 | Shut off Head | 30 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 65 | % | Pump Shaft | STS431
14 | Min. Flow | 900 | ℓ/min | Coupling | STS304
15 | Max. Flow | 2300 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 125 | mm | Strainer | STS304
17 | Out Dia. | 178mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 7.5 | kW | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 19.6 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 1 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 618 | mm | Pump | 25.1 | kg
37 | Motor | 645 | mm | Motor | 52 | kg
38 | Total | 1263 | mm | Total | 77.1 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(95-2-B)
Submersible Motor Pump Data Sheet
1 | Model | PSS-95-2-B_MF6-15033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 30 | m | Discharge Piece | STS304
10 | Rated Capacity | 1600 | ℓ/min | Impeller | STS304
11 | Shut off Head | 50 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 70 | % | Pump Shaft | STS431
14 | Min. Flow | 800 | ℓ/min | Coupling | STS304
15 | Max. Flow | 2200 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 125 | mm | Strainer | STS304
17 | Out Dia. | 178mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 11 | kW | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 28.9 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 2 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 746 | mm | Pump | 28.7 | kg
37 | Motor | 711 | mm | Motor | 58 | kg
38 | Total | 1457 | mm | Total | 86.7 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(95-3-BB)
Submersible Motor Pump Data Sheet
1 | Model | PSS-95-3-BB_MF6-20033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 38 | m | Discharge Piece | STS304
10 | Rated Capacity | 1600 | ℓ/min | Impeller | STS304
11 | Shut off Head | 60 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 70 | % | Pump Shaft | STS431
14 | Min. Flow | 800 | ℓ/min | Coupling | STS304
15 | Max. Flow | 2300 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 125 | mm | Strainer | STS304
17 | Out Dia. | 178mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 15 | kW | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 37.3 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 3 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 874 | mm | Pump | 32.3 | kg
37 | Motor | 777 | mm | Motor | 64 | kg
38 | Total | 1651 | mm | Total | 96.3 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## DataSheet(95-3-B)
Submersible Motor Pump Data Sheet
1 | Model | PSS-95-3-B_MF6-25033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 50 | m | Discharge Piece | STS304
10 | Rated Capacity | 1600 | ℓ/min | Impeller | STS304
11 | Shut off Head | 80 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 70 | % | Pump Shaft | STS431
14 | Min. Flow | 800 | ℓ/min | Coupling | STS304
15 | Max. Flow | 2300 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 125 | mm | Strainer | STS304
17 | Out Dia. | 178mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 18.5 | kW | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 46 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 3 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 874 | mm | Pump | 32.3 | kg
37 | Motor | 841 | mm | Motor | 70 | kg
38 | Total | 1715 | mm | Total | 102.3 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## DataSheet(95-4-AB)
Submersible Motor Pump Data Sheet
1 | Model | PSS-95-4-AB_MF6-30033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 60 | m | Discharge Piece | STS304
10 | Rated Capacity | 1600 | ℓ/min | Impeller | STS304
11 | Shut off Head | 100 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 70 | % | Pump Shaft | STS431
14 | Min. Flow | 800 | ℓ/min | Coupling | STS304
15 | Max. Flow | 2200 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 125 | mm | Strainer | STS304
17 | Out Dia. | 178mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 22 | kW | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 55.4 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 4 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1003 | mm | Pump | 35.9 | kg
37 | Motor | 907 | mm | Motor | 76 | kg
38 | Total | 1910 | mm | Total | 111.9 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## DataSheet(95-5-B)
Submersible Motor Pump Data Sheet
1 | Model | PSS-95-5-B_MF6-40033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 85 | m | Discharge Piece | STS304
10 | Rated Capacity | 1600 | ℓ/min | Impeller | STS304
11 | Shut off Head | 139 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 70 | % | Pump Shaft | STS431
14 | Min. Flow | 800 | ℓ/min | Coupling | STS304
15 | Max. Flow | 2200 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 125 | mm | Strainer | STS304
17 | Out Dia. | 178mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 30 | kW | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 74.6 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 5 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1131 | mm | Pump | 39.5 | kg
37 | Motor | 1036 | mm | Motor | 92 | kg
38 | Total | 2167 | mm | Total | 131.5 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## DataSheet(95-6)
Submersible Motor Pump Data Sheet
1 | Model | PSS-95-6_MF6-50033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 120 | m | Discharge Piece | STS304
10 | Rated Capacity | 1600 | ℓ/min | Impeller | STS304
11 | Shut off Head | 175 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 90 | % | Pump Shaft | STS431
14 | Min. Flow | 800 | ℓ/min | Coupling | STS304
15 | Max. Flow | 2300 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 125 | mm | Strainer | STS304
17 | Out Dia. | 178mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 37 | kW | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 95 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 6 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1259 | mm | Pump | 43 | kg
37 | Motor | 1405 | mm | Motor | 136 | kg
38 | Total | 2664 | mm | Total | 179 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
DIEMENSION(mm)
MODEL | MOTOR | P.L |  |  | M.L |  |  | T.L
PSS-95-1-A | MF6-7533 | 618 |  |  | 615 |  |  | 1233
PSS-95-1 | MF6-10033 | 618 |  |  | 645 |  |  | 1263
PSS-95-2-B | MF6-15033 | 746 |  |  | 711 |  |  | 1457
PSS-95-3-BB | MF6-20033 | 874 |  |  | 777 |  |  | 1651
PSS-95-3-B | MF6-25033 | 874 |  |  | 841 |  |  | 1715
PSS-95-3 | MF6-30033 | 874 |  |  | 907 |  |  | 1781
PSS-95-4-AB | MF6-30033 | 1003 |  |  | 907 |  |  | 1910
PSS-95-5-B | MF6-40033 | 1131 |  |  | 1036 |  |  | 2167
PSS-95-5 | MF6-50033 | 1131 |  |  | 1405 |  |  | 2536
PSS-95-6 | MF6-50033 | 1259 |  |  | 1405 |  |  | 2664
WEIGHT(kg)
MODEL | MOTOR | PUMP |  |  | MOTOR |  |  | TOTAL
PSS-95-1-A | MF6-7533 | 25.1 |  |  | 48 |  |  | 73.1
PSS-95-1 | MF6-10033 | 25.1 |  |  | 52 |  |  | 77.1
PSS-95-2-B | MF6-15033 | 28.7 |  |  | 58 |  |  | 86.7
PSS-95-3-BB | MF6-20033 | 32.3 |  |  | 64 |  |  | 96.3
PSS-95-3-B | MF6-25033 | 32.3 |  |  | 70 |  |  | 102.3
PSS-95-3 | MF6-30033 | 32.3 |  |  | 76 |  |  | 108.3
PSS-95-4-AB | MF6-30033 | 35.9 |  |  | 76 |  |  | 111.9
PSS-95-5-B | MF6-40033 | 39.5 |  |  | 92 |  |  | 131.5
PSS-95-5 | MF6-50033 | 39.5 |  |  | 136 |  |  | 175.5
PSS-95-6 | MF6-50033 | 43 |  |  | 136 |  |  | 179
※MOTOR MAKER : FRANKLIN ELECTRIC U.S.A
※DISCHARGE CONNECTION : 5" (125mm)
|  |  | TYPE |  |  | SUBMERSIBLE PUMP
MODEL
SERVICE
|  |  | SCALE:N/S |  |  |  | 3rd. ANGLE PROJECT
Outline Drawing
of PSS-95 Series
P.L
M.L
T.L

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO | PART NAME |  |  |  | MATERIAL | Q'TY
1 | Discharge |  |  |  | STS304 | 1
2 | Spring |  |  |  |  | 1
3 | Upper Retainer |  |  |  |  | 1
4 | Lower Retainer |  |  |  |  | 1
5 | O-ring |  |  |  | NBR | 1
6 | Diffuser |  |  |  | STS304 | Stages
7 | Neck Ring |  |  |  | STS304+NBR | Stages
8 | Split Cone Nut |  |  |  | STS304 | Stages
9 | Ring Of Impeller |  |  |  |  | Stages
10 | Impeller |  |  |  |  | Stages
11 | Space Washer |  |  |  | MoO2+PTFE | 1
12 | Nut for Stop Ring |  |  |  | STS304 | 1
13 | Shaft |  |  |  | STS431 | 1
14 | Screw |  |  |  | STS304 | 2
15 | Key |  |  |  |  | 2
16 | Strainer |  |  |  |  | 1
17 | Cable Guard |  |  |  |  | 1~2
18 | Valve Cup |  |  |  |  | 1
19 | Valve Seat |  |  |  |  | 1
20 | Bearing |  |  |  | NBR | Stages
21 | Spilt Cone |  |  |  | STS304 | Stages
22 | Bearing |  |  |  | NBR | 1
23 | Stop Ring |  |  |  | STS304 | 1
24 | Bottom diffuser |  |  |  |  | 1
25 | Stap |  |  |  |  | 4
26 | Coupling |  |  |  | STS304 | 1
27 | Spring Washer |  |  |  | STS304 | 4
28 | Nut |  |  |  |  | 4
29 | O-ring |  |  |  | NBR | 1
30 | Pump Base |  |  |  | STS304 | 1
| TYPE |  | SUBMERSIBEL PUMP
MODEL
SERVICE
| SCALE:N/S |  |  | 3rd. ANGLE PROJECT
Sectional Drawing
of PSS-95 Series

## Test Report(95-1-A)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 504 | 908 | 1200 | 1510 | 1802 | 2107
Dis. Head | (m) | 22.1 | 18.7 | 15 | 12.9 | 10.5 | 6.5 | 1.5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.023905 | 0.077587 | 0.13551 | 0.21457 | 0.30558 | 0.41778
Total Head | (m) | 24.6 | 21.2239 | 17.5776 | 15.5355 | 13.2146 | 9.3056 | 4.4178
Water Power | (㎾) | 0 | 1.7436 | 2.6016 | 3.0387 | 3.2525 | 2.7333 | 1.5172
Shaft Power | (㎾) | 3.811 | 4.0478 | 4.2624 | 4.6176 | 4.8914 | 4.9358 | 4.7138
Pump Eff. | (%) | 0 | 43.0749 | 61.0349 | 65.8079 | 66.4943 | 55.3769 | 32.1873
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 10.81 | 11.19 | 11.57 | 12.21 | 12.73 | 12.76 | 12.39
Motor Input | (㎾) | 5.15 | 5.47 | 5.76 | 6.24 | 6.61 | 6.67 | 6.37
Motor Eff. | (%) | 74 | 74 | 74 | 74 | 74 | 74 | 74
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 1600 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 5.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 11 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 125 | 2.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 15 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 74 | Maker | FRANKLIN | Turbin | 12
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-95-1-A_MF6-7533 |  | Customer |  |  |  | 2 |  | 2008.02.27
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(95-1)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 506 | 1000 | 1407 | 1762 | 2110 | 2565
Dis. Head | (m) | 30 | 26.5 | 20 | 16.5 | 14.5 | 11 | 2.5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.024095 | 0.094106 | 0.1863 | 0.29217 | 0.41897 | 0.61915
Total Head | (m) | 32.5 | 29.0241 | 22.5941 | 19.1863 | 17.2922 | 13.919 | 5.6191
Water Power | (㎾) | 0 | 2.3938 | 3.6828 | 4.4002 | 4.9664 | 4.7872 | 2.3493
Shaft Power | (㎾) | 5.3976 | 5.9202 | 6.0208 | 6.5988 | 7.215 | 7.3398 | 7.0122
Pump Eff. | (%) | 0 | 40.4353 | 61.1684 | 66.6819 | 68.8346 | 65.2218 | 33.5036
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 14 | 14.91 | 15.02 | 16.06 | 17.19 | 17.43 | 16.85
Motor Input | (㎾) | 6.92 | 7.59 | 7.719 | 8.46 | 9.25 | 9.41 | 8.99
Motor Eff. | (%) | 78 | 78 | 78 | 78 | 78 | 78 | 78
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 1600 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 7.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 17 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 125 | 2.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 19.6 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 78 | Maker | FRANKLIN | Turbin | 12
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-95-1_MF6-10033 |  | Customer |  |  |  | 2 |  | 2008.02.21
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(95-2-B)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 511 | 1000 | 1501 | 1829 | 2006 | 2469
Dis. Head | (m) | 50 | 45 | 37 | 30.5 | 23.5 | 19 | 2.5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.024573 | 0.094106 | 0.21202 | 0.31481 | 0.37869 | 0.57367
Total Head | (m) | 52.5 | 47.5246 | 39.5941 | 33.212 | 26.3148 | 21.8787 | 5.5737
Water Power | (㎾) | 0 | 3.9585 | 6.4538 | 8.1258 | 7.8452 | 7.1538 | 2.2431
Shaft Power | (㎾) | 8.5734 | 9.5518 | 10.1293 | 11.2601 | 11.5328 | 11.5167 | 10.6907
Pump Eff. | (%) | 0 | 41.442 | 63.7148 | 72.1643 | 68.025 | 62.1171 | 20.9819
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 21.17 | 22.88 | 23.87 | 25.94 | 26.42 | 26.38 | 24.92
Motor Input | (㎾) | 10.69 | 11.91 | 12.63 | 14.04 | 14.38 | 14.36 | 13.33
Motor Eff. | (%) | 80.2 | 80.2 | 80.2 | 80.2 | 80.2 | 80.2 | 80.2
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 1600 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 11 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 30 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 125 | 2.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 28.9 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 80.2 | Maker | FRANKLIN | Turbin | 14 | 14
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-95-2-B_MF6-15033 |  | Customer |  |  |  | 2 |  | 2008.02.27
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(95-3-BB)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 507 | 1016 | 1505 | 1822 | 2017 | 2614
Dis. Head | (m) | 60.5 | 55 | 45 | 37.5 | 32.5 | 28 | 3.1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.02419 | 0.097142 | 0.21315 | 0.3124 | 0.38285 | 0.64303
Total Head | (m) | 63 | 57.5242 | 47.5971 | 40.2132 | 35.3124 | 30.8829 | 6.243
Water Power | (㎾) | 0 | 4.7539 | 7.8825 | 9.8649 | 10.4873 | 10.1534 | 2.66
Shaft Power | (㎾) | 10.8038 | 11.881 | 12.3053 | 13.6272 | 14.3045 | 14.4758 | 13.3008
Pump Eff. | (%) | 0 | 40.0124 | 64.0576 | 72.3912 | 73.3147 | 70.1402 | 19.9991
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 26.1 | 27.85 | 28.64 | 31.02 | 32.16 | 32.48 | 30.41
Motor Input | (㎾) | 13.24 | 14.56 | 15.08 | 16.7 | 17.53 | 17.74 | 16.3
Motor Eff. | (%) | 81.6 | 81.6 | 81.6 | 81.6 | 81.6 | 81.6 | 81.6
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 1600 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 15 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 38 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 125 | 2.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 37.3 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 81.6 | Maker | FRANKLIN | Turbin | 14 | 14
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-95-3-BB_MF6-20033 |  | Customer |  |  |  | 2 |  | 2008.02.29
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(95-3-B)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 505 | 1008 | 1507 | 1807 | 2005 | 2570
Dis. Head | (m) | 80.5 | 74.5 | 62 | 51 | 42.5 | 35 | 3
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.023999 | 0.095618 | 0.21372 | 0.30728 | 0.37831 | 0.62156
Total Head | (m) | 83 | 77.024 | 64.5956 | 53.7137 | 45.3073 | 37.8783 | 6.1216
Water Power | (㎾) | 0 | 6.3402 | 10.6133 | 13.1943 | 13.3449 | 12.3792 | 2.5644
Shaft Power | (㎾) | 13.7842 | 15.2192 | 16.2688 | 17.9744 | 18.3926 | 18.4172 | 16.3344
Pump Eff. | (%) | 0 | 41.6594 | 65.2373 | 73.406 | 72.5555 | 67.2154 | 15.6993
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 33.03 | 35.46 | 37.2 | 40.26 | 41.04 | 40.97 | 37.45
Motor Input | (㎾) | 16.81 | 18.56 | 19.84 | 21.92 | 22.43 | 22.46 | 19.92
Motor Eff. | (%) | 82 | 82 | 82 | 82 | 82 | 82 | 82
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 1600 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 18.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 50 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 125 | 2.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 46.0 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 82 | Maker | FRANKLIN | Turbin | 14 | 14
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-95-3-B_MF6-25033 |  | Customer |  |  |  | 2 |  | 2008.03.03
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(95-4-AB)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 499 | 1013 | 1506 | 1846 | 2005 | 2553
Dis. Head | (m) | 103 | 95 | 79 | 65.5 | 51.5 | 43 | 3
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.023433 | 0.096569 | 0.21344 | 0.32069 | 0.37831 | 0.61337
Total Head | (m) | 105.5 | 97.5234 | 81.5966 | 68.2134 | 54.3207 | 45.8783 | 6.1134
Water Power | (㎾) | 0 | 7.9323 | 13.4731 | 16.7449 | 16.345 | 14.9937 | 2.544
Shaft Power | (㎾) | 17.4616 | 19.0806 | 20.5922 | 22.6324 | 23.1032 | 22.9298 | 20.2783
Pump Eff. | (%) | 0 | 41.5724 | 65.4284 | 73.9864 | 70.7477 | 65.3898 | 12.5455
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 40.15 | 42.84 | 45.51 | 49.31 | 50.1 | 49.81 | 45.13
Motor Input | (㎾) | 21.14 | 23.1 | 24.93 | 27.4 | 27.97 | 27.76 | 24.55
Motor Eff. | (%) | 82.6 | 82.6 | 82.6 | 82.6 | 82.6 | 82.6 | 82.6
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 1600 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 22 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 60 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 125 | 2.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 55.4 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 82.6 | Maker | FRANKLIN | Turbin | 14 | 14
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-95-4-AB_MF6-30033 |  | Customer |  |  |  | 2 |  | 2008.03.04
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(95-5-B)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 510 | 1010 | 1500 | 1790 | 2030 | 2575
Dis. Head | (m) | 139 | 128 | 106 | 87 | 77 | 58 | 1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.024477 | 0.095998 | 0.21174 | 0.30153 | 0.3878 | 0.62398
Total Head | (m) | 142 | 131.0245 | 109.096 | 90.2117 | 80.3015 | 61.3878 | 4.624
Water Power | (㎾) | 0 | 10.8921 | 17.9605 | 22.0568 | 23.4296 | 20.3126 | 1.9408
Shaft Power | (㎾) | 25.0884 | 27.4896 | 28.8972 | 31.6296 | 32.292 | 32.1264 | 28.3176
Pump Eff. | (%) | 0 | 39.6225 | 62.153 | 69.7346 | 72.5554 | 63.2272 | 6.8537
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 57 | 61 | 64 | 68 | 70 | 69 | 63
Motor Input | (㎾) | 30.3 | 33.2 | 34.9 | 38.2 | 39 | 38.8 | 34.2
Motor Eff. | (%) | 82.8 | 82.8 | 82.8 | 82.8 | 82.8 | 82.8 | 82.8
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 1600 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 30 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 85 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 125 | 3
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 75 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 82.8 | Maker | FRANKLIN | Turbin | 7
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-95-5-B_MF6-40033 |  | Customer |  |  |  | 2 |  | 2008.03.21
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(95-6)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 551 | 1058 | 1519 | 2034 | 2124 | 2596
Dis. Head | (m) | 177.5 | 176 | 160 | 138 | 107 | 97 | 2
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.028571 | 0.10534 | 0.21714 | 0.38933 | 0.42455 | 0.6342
Total Head | (m) | 180.5 | 179.0286 | 163.1053 | 141.2171 | 110.3893 | 100.4245 | 5.6342
Water Power | (㎾) | 0 | 16.0791 | 28.1282 | 34.9649 | 36.5987 | 34.7682 | 2.3841
Shaft Power | (㎾) | 33.0802 | 34.1943 | 37.2795 | 39.422 | 42.9357 | 43.2785 | 39.7648
Pump Eff. | (%) | 0 | 47.0227 | 75.4521 | 88.694 | 85.2407 | 80.3359 | 5.9955
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 68 | 71 | 76 | 77 | 87 | 88 | 81
Motor Input | (㎾) | 38.6 | 39.9 | 43.5 | 46 | 50.1 | 50.5 | 46.4
Motor Eff. | (%) | 85.7 | 85.7 | 85.7 | 85.7 | 85.7 | 85.7 | 85.7
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 1600 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 37 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 120 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 125 | 3
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 95 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 85.7 | Maker | FRANKLIN | Turbin | 6
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-95-6_MF6-50033 |  | Customer |  |  |  | 2 |  | 2008.03.20
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification