## Datasheet(PU-1700N)
PUMP DATA SHEET
| Model | PU-1700N | Title |  |  | Sheet No.
1 | Customer |  |  | Agent No.
2 | Location |  |  | Date Issued
3 | Item No. |  |  | Plant Name
4 | Service |  |  | Quantity |  | Location | ■In, □Out
5 | OPERATING CONDITION
6 | Liquid |  | Flow | 300 | ℓ/min | NPSHav | mAq
7 | Pumping Temp | AMB. ℃ | Suct.Head | 6 | m | Concentration | %
8 | Sp. Gr. @P.T | 1 | Disch.Head | 3 | m | Solid
9 | Vap. Press @P.T | Kg/㎠A | Total Head | 9 | m | Corros.or Erros
10 | Visc @P.T | Cp
11 | [5 empty] | MATERIALS
12 | ■ Horizontal | □ Vertical | Efficiency | 30 | % | (Parts' Name) | Symbol(KS)
13 | Number of Stages | 1 Stage | Rated Power | 2200 | W | Impeller | C3771BD
14 | Speed | 3400 | NPSHre |  | mAq | Shaft | SM20C+STS430
15 | Rotation | □ CW, ■ CCW | Column Head |  | m | Casing | GC150
16 | Flange | Size(Dia) | Rating | Face | Position | Suct.Flange | GC200
17 | Suction | 50mm |  | ■ FF, □ RF | □End □Top ■Side | Disch.Flange | GC200
18 | Discharge | 50mm |  | ■ FF, □ RF | ■Top, □Side | Plate | STS304
19 | Impeller Type | Semi Open | ■Single Suct. | □Double Suct. | HYDROSTATIC
20 | Flow Direction | ■Radial | □ Mixed | □ Axial | Casing | 5 Kg/㎠ | 3 Min.
21 | Shaft Seal | □ G/Packing | ■ M/Seal
22 | Shaft Sleeve | □Yes, □No
23 | Mounting | □ Foot | □ Centerline | □ Bracket | TESTING
24 | Lubrication Type | □ Grease | □ Oil Bath |  | (Items) |  | (witness)
25 | Cooling | □ Stuff.Box | □B/R Housing | □ No. Cooling | Run Perform. | ■ Yes □ No | □Yes □No
26 | Radial Bearings | 6204ZZ | Thrust Bearing | 6305ZZ | Hydrostatic | ■ Yes □ No | □Yes □No
27 | PUMP DRIVER |  |  |  |  | SPARE PARTS
28 | Motor | V/Phase/Hz | 440 | 3 | 60 | Impeller | Set(S)
29 | Maker | WILO Pumps Ltd. |  |  |  | Shaft | Set(S)
30 | Type | INDUCTION MOTOR |  |  |  | Shaft Sleeve | Set(S)
31 | Power | 1700W |  |  |  | Casing Ring | Set(S)
32 | Pole & Speed | 2 p 3400 rpm | Insulation Class | ■ B | □ E | Bearing(R+T) | Set(S)
33 | ACCESSORIES |  |  |  |  | Bearing(Journal) | Set(S)
34 | □Base Plate | □ Cast Iron | □Steel Plate |  | □ Drain Rim | M/Seal | Set(S)
35 | □Foundation Bolts & Nuts |  |  |  |  | Casing Gasket | Set(S)
36 | Coupling | □ Sun Flex | □ WOODS | □ Grid | □Coupling Guard | Oil Seal | Set(S)
37 | □Press. Gauge | □Suct.Vacuum □Suct.Compound □Suct.Press □Disch.Press |  |  |  | Coupling | Set(S)
38 | □Collar or Plug for Drain & Air Vent. |  |  |  |  | Coupling Rubber | Set(S)
39 | □Sealing Flushing Pipe |  | □ Cooling Piping |  |  | Name Plate | Set(S)
40 |  | Maker | N.E.K | Model & Size | Φ 18 |  | Set(S)
41 | Mechanical Seal | Type | EA103-18 | Cooler | □Yes, ■No | WEIGHT
42 | [5 empty] | Pump / Bed | Kg
43 | □ Companion Flange |  |  |  |  | Driver | Kg
44 | □ Special Tools |  |  |  |  | Total Wt. | 43.5 Kg

## Outline Drawing(PU-1700N)
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
PUMP | CAPACITY | ℓ/min | 300 |  | MOTOR | OUTPUT |  |  |  | W | 2200
| TOTAL HEAD | m | 9 |  |  | VOLTAGE |  |  |  | V | 440
| SUCTION BORE | mm | Ø | 50 |  | FREQUENCY |  |  |  | Hz | 60
| DISCHARGE BORE | mm | Ø | 50 |  | No. OF REVOLUTION |  |  |  | r.p.m | 3400
| LIQUID | WATER |  |  |  | TYPE |  |  |  | ONE PHASE INDUCTION
| MAKER | WILO Pumps Ltd. |  |  |  | MAKER |  |  |  | WILO Pumps Ltd.
[7 empty] | TYPE |  | AGRICULTURAL PUMP
[7 empty] | MODEL |  | PU-1700N
SERVICE
SCALE:N/S
OUTLINE DRAWING
of PU TYPE

## Sectional Drawing(PU-1700N)
Sheet No.
CUSTOMER
ITEM No.
DATE
NO. | PARTS NAME | MATERIALS |  |  |  |  | Q'ty(EA)
|  | KS | ASTM | DIN
1 | CASING | GC150 | class No.25 | GG15 |  |  | 1
2 | MOTOR | - | - | - |  |  | 1
3 | BERAING | 6305ZZ | - | - |  |  | 1
4 | BERAING | 6204ZZ | - | - |  |  | 1
5 | END BRACKET(A) | GC150 | class No.25 | GG15 |  |  | 1
6 | END BRACKET(B) | GC150 | class No.25 | GG15 |  |  | 1
7 | Mechanical Seal | NBR+CARBON+CERAMIC | - | - |  |  | 1
8 | IMPELLER | C3771BD | - | - |  |  | 1
9 | PLATE | STS304 | C37700 | CuZn40Pb2 |  |  | 1
10 | DISCHARGE FLANGE | GC200 | class No.30 | GG20 |  |  | 1
11 | SUCTION FLANGE | GC200 | class No.30 | GG20 |  |  | 1
12 | PACKING | NBR607 | - | - |  |  | 1
13 | CHECK VALVE | NBR510 | - | - |  |  | 1
14 | DRAIN CAP | PBT | - | - |  |  | 1
15 | BASE PLATE | SPCC | - | - |  |  | 1
16
|  |  |  | TYPE |  | AGRICULTURAL PUMP
|  |  |  | MODEL |  | PU-1700N
SERVICE
SCALE:N/S
SECTIONAL DRAWING
of PU TYPE

## Test Report
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 96 | 155 | 207 | 286 | 312 | 318 | 322
Dis. Head | (m) | 23.7 | 20 | 17 | 14 | 8 | 5 | 3 | 1.2
Suc. Head | (m) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Speed Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Head | (m) | 29.7 | 26 | 23 | 20 | 14 | 11 | 9 | 7.2
Water Power | (㎾) | 0 | 0.40685 | 0.5811 | 0.67482 | 0.65265 | 0.55942 | 0.46651 | 0.3779
Shaft Power | (㎾) | 1.4817 | 1.7236 | 1.8655 | 1.95 | 1.9893 | 2.0525 | 1.9491 | 1.8835
Pump Eff. | (%) | 0 | 23.604 | 31.1496 | 34.6069 | 32.8078 | 27.2559 | 23.9339 | 20.0632
Speed | (rpm) | 3482 | 3456 | 3436 | 3431 | 3420 | 3416 | 3436 | 3443
Voltage | (V) | 440 | 440 | 440 | 440 | 440 | 440 | 440 | 440
Current | (A) | 2.9 | 3.25 | 3.46 | 3.58 | 3.62 | 3.72 | 3.57 | 3.47
Motor Input | (㎾) | 1.807 | 2.102 | 2.275 | 2.378 | 2.426 | 2.503 | 2.377 | 2.297
Motor Eff. | (%) | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 300 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 9 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 | 50 | 50 | 0
Efficiency |  | (%) | Volt. (V) | 440 | Current(A) | 4.5 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 82 | Maker | WILO | Turbin | 20 | 7
Item No. | N.A |  | Serial No. | X2 | Inspector | K.I.H | Run (Hr) | B/R (℃) | Test Date
Model | PU-1700N |  | Customer |  | X1 |  | 1
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification