## Datasheet
PUMP DATA SHEET
| Model | PU-602U | Title |  |  | Sheet No.
1 | Customer |  |  | Agent No.
2 | Location |  |  | Date Issued
3 | Item No. |  |  | Plant Name
4 | Service |  |  | Quantity |  | Location | ■In, □Out
5 | OPERATING CONDITION
6 | Liquid | Water | Flow | 170 | ℓ/min | NPSHav | mAq
7 | Pumping Temp | AMB. ℃ | Suct.Head | 6 | m | Concentration | %
8 | Sp. Gr. @P.T | 1 | Disch.Press | 1 | m | Solid
9 | Vap. Press @P.T | Kg/㎠A | Total Head | 7 | m | Corros.or Erros
10 | Visc @P.T | Cp
11 | [5 empty] | MATERIALS
12 | ■ Horizontal | □ Vertical | Efficiency | 40 | % | (Parts' Name) | Symbol(KS)
13 | Number of Stages | 1 Stage | Rated Power | 600 | W | Impeller | C3771BD
14 | Speed | 3400 rpm | NPSHre |  | mAq | Shaft | STS314
15 | Rotation | □ CW, ■ CCW | Column Head |  | m | Casing | GC150
16 | Flange | Size(Dia) | Rating | Face | Position | Suct.Flange | GC150
17 | Suction | 40mm |  | ■ FF, □ RF | □End □Top ■Side | Disch.Flange | GC150
18 | Discharge | 40mm |  | ■ FF, □ RF | ■Top, □Side | Plate | PE
19 | Impeller Type | SEMI OPEN | ■Single Suct. | □Double Suct. | HYDROSTATIC
20 | Flow Direction | ■ Radial | □ Mixed | □ Axial | Casing | 3 Kg/㎠ | 3 Min.
21 | Shaft Seal | □ G/Packing | ■ M/Seal
22 | Shaft Sleeve | □Yes, □No
23 | Mounting | □ Foot | □ Centerline | □ Bracket | TESTING
24 | Lubrication Type | □ Grease | □ Oil Bath |  | (Items) |  | (witness)
25 | Cooling | □ Stuff.Box | □B/R Housing | □ No. Cooling | Run Perform. | ■ Yes □ No | □Yes □No
26 | Radial Bearings | 6202ZZ | Thrust Bearing | 6202ZZ | Hydrostatic | ■ Yes □ No | □Yes □No
27 | PUMP DRIVER |  |  |  |  | SPARE PARTS
28 | Motor | V/Phase/Hz | 380 | 3 | 60 | Impeller | Set(S)
29 | Maker | WILO Pumps Ltd. |  |  |  | Shaft | Set(S)
30 | Type | INDUCTION MOTOR |  |  |  | Shaft Sleeve | Set(S)
31 | Power | 600W |  |  |  | Casing Ring | Set(S)
32 | Pole & Speed | 2 p 3400 rpm | Insulation Class | ■ F | □ E | Bearing(R+T) | Set(S)
33 | ACCESSORIES |  |  |  |  | Bearing(Journal) | Set(S)
34 | □Base Plate | □ Cast Iron | □Steel Plate |  | □ Drain Rim | M/Seal | Set(S)
35 | □Foundation Bolts & Nuts |  |  |  |  | Casing Gasket | Set(S)
36 | Coupling | □ Sun Flex | □ WOODS | □ Grid | □Coupling Guard | Oil Seal | Set(S)
37 | □Press. Gauge | □Suct.Vacuum □Suct.Compound □Suct.Press □Disch.Press |  |  |  | Coupling | Set(S)
38 | □Collar or Plug for Drain & Air Vent. |  |  |  |  | Coupling Rubber | Set(S)
39 | □Sealing Flushing Pipe |  | □ Cooling Piping |  |  | Name Plate | Set(S)
40 |  | Maker | N.E.K | Model & Size | Φ 15 |  | Set(S)
41 | Mechanical Seal | Type | EA104-15 | Cooler | □Yes, ■No | WEIGHT
42 | [5 empty] | Pump / Bed | Kg
43 | □ Companion Flange |  |  |  |  | Driver | Kg
44 | □ Special Tools |  |  |  |  | Total Wt. | 16.5 Kg

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
PUMP | CAPACITY | ℓ/min | 170 |  | MOTOR | OUTPUT |  |  |  | W | 600
| TOTAL HEAD | m | 7 |  |  | VOLTAGE |  |  |  | V | 220
| SUCTION BORE | mm | Ø | 40 |  | FREQUENCY |  |  |  | Hz | 60
| DISCHARGE BORE | mm | Ø | 40 |  | No. OF REVOLUTION |  |  |  | r.p.m | 3400
| LIQUID | WATER |  |  |  | TYPE |  |  |  | ONE PHASE INDUCTION
| MAKER | WILO-LG |  |  |  | MAKER |  |  |  | WILO-LG
[7 empty] | TYPE |  | AGRICULTURAL PUMP
[7 empty] | MODEL |  | PU-602M
SERVICE
SCALE:N/S
OUTLINE DRAWING
of PU TYPE

## Sectioal Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO. | PARTS NAME | MATERIALS |  |  |  |  | Q'ty(EA)
|  | KS | ASTM | DIN
1 | CASING | GC150 | class No.25 | GG15 |  |  | 1
2 | MOTOR | - | - | - |  |  | 1
3 | CAPACITOR COVER | ABS | - | - |  |  | 1
4 | END BRACKET(A) | GC150 | class No.25 | GG15 |  |  | 1
5 | END BRACKET(B) | ALDC8 | - | - |  |  | 1
6 | Mechanical Seal | NBR+CARBON+CERAMIC | - | - |  |  | 1
7 | IMPELLER | C3771BD | C37700 | CuZn40Pb2 |  |  | 1
8 | DISCHARGE FLANGE | GC150 | class No.25 | GG15 |  |  | 1
9 | SUCTION FLANGE | GC150 | class No.25 | GG15 |  |  | 1
10 | PACKING | NBR607 | - | - |  |  | 2
11 | CHECK VALVE | NBR610 | - | - |  |  | 1
12 | DRAIN CAP | PBT | - | - |  |  | 1
13 | BASE PLATE | HDPE | - | - |  |  | 1
|  |  |  | TYPE |  | AGRICULTURAL PUMP
|  |  |  | MODEL |  | PU-602M
SERVICE
SCALE:N/S
SECTIONAL DRAWING
of PU TYPE

## Test Report
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 71 | 95 | 114 | 149 | 174 | 184 | 190
Dis. Head | (m) | 12.5 | 10 | 9 | 8 | 6 | 4 | 2 | 0
Suc. Head | (m) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Speed Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Head | (m) | 18.5 | 16 | 15 | 14 | 12 | 10 | 8 | 6
Water Power | (㎾) | 0 | 0.18517 | 0.23228 | 0.26015 | 0.29144 | 0.28362 | 0.23994 | 0.18582
Shaft Power | (㎾) | 0.39411 | 0.47112 | 0.5066 | 0.53228 | 0.58361 | 0.61381 | 0.6191 | 0.59947
Pump Eff. | (%) | 0 | 39.3038 | 45.8493 | 48.8747 | 49.9377 | 46.2061 | 38.7556 | 30.9974
Speed | (rpm) | 3484 | 3456 | 3443 | 3431 | 3411 | 3396 | 3392 | 3399
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 1.31 | 1.4 | 1.44 | 1.47 | 1.55 | 1.59 | 1.59 | 1.56
Motor Input | (㎾) | 0.522 | 0.624 | 0.671 | 0.705 | 0.773 | 0.813 | 0.82 | 0.794
Motor Eff. | (%) | 75.5 | 75.5 | 75.5 | 75.5 | 75.5 | 75.5 | 75.5 | 75.5
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 150 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 0.6 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 10 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 | 40 | 40
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) |  | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 75.5 | Maker | WILO | Turbin | 22 | 10
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PU-602U |  | Customer |  |  |  | 1
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification