## Datasheet
PUMP DATA SHEET
| Model | PU-S990M | Title |  |  | Sheet No.
1 | Customer |  |  | Agent No.
2 | Location |  |  | Date Issued
3 | Item No. |  |  | Plant Name
4 | Service |  |  | Quantity |  | Location | ■In, □Out
5 | OPERATING CONDITION
6 | Liquid |  | Flow | 280 | ℓ/min (Ht=9m 일때) | NPSHav | mAq
7 | Pumping Temp | AMB. ℃ | Suct.Head | 6 | m | Concentration | %
8 | Sp. Gr. @P.T | 1 | Disch.Head | 3 | m | Solid
9 | Vap. Press @P.T | Kg/㎠A | Total Head | 9 | m | Corros.or Erros
10 | Visc @P.T | Cp
11 | [5 empty] | MATERIALS
12 | ■ Horizontal | □ Vertical | Efficiency | 40 | % | (Parts' Name) | Symbol(KS)
13 | Number of Stages | 1 Stage | Rated Power | 990 | W | Impeller | STS304
14 | Speed | 3400 | NPSHre |  | mAq | Shaft | SM20C+STS316
15 | Rotation | □ CW, ■ CCW | Column Head |  | m | Casing | PP
16 | Flange | Size(Dia) | Rating | Face | Position | Suct.Flange | PP
17 | Suction | 50mm |  | □ FF, □ RF | ■End □Top □Side | Disch.Flange | PP
18 | Discharge | 50mm |  | □ FF, □ RF | ■Top, □Side | Plate | STS304
19 | Impeller Type | Semi Open | ■Single Suct. | □Double Suct. | HYDROSTATIC
20 | Flow Direction | ■Radial | □ Mixed | □ Axial | Casing | 4 Kg/㎠ | 3 Min.
21 | Shaft Seal | □ G/Packing | ■ M/Seal
22 | Shaft Sleeve | □Yes, □No
23 | Mounting | □ Foot | □ Centerline | □ Bracket | TESTING
24 | Lubrication Type | □ Grease | □ Oil Bath |  | (Items) |  | (witness)
25 | Cooling | □ Stuff.Box | □B/R Housing | □ No. Cooling | Run Perform. | ■ Yes □ No | □Yes □No
26 | Radial Bearings | 6202ZZ | Thrust Bearing | 6305ZZ | Hydrostatic | ■ Yes □ No | □Yes □No
27 | PUMP DRIVER |  |  |  |  | SPARE PARTS
28 | Motor | V/Phase/Hz | 220 | 1 | 60 | Impeller | Set(S)
29 | Maker | WILO Pumps Ltd. |  |  |  | Shaft | Set(S)
30 | Type | INDUCTION MOTOR |  |  |  | Shaft Sleeve | Set(S)
31 | Power | 990W |  |  |  | Casing Ring | Set(S)
32 | Pole & Speed | 2 p 3400 rpm | Insulation Class | ■ B | □ E | Bearing(R+T) | Set(S)
33 | ACCESSORIES |  |  |  |  | Bearing(Journal) | Set(S)
34 | □Base Plate | □ Cast Iron | □Steel Plate |  | □ Drain Rim | M/Seal | Set(S)
35 | □Foundation Bolts & Nuts |  |  |  |  | Casing Gasket | Set(S)
36 | Coupling | □ Sun Flex | □ WOODS | □ Grid | □Coupling Guard | Oil Seal | Set(S)
37 | □Press. Gauge | □Suct.Vacuum □Suct.Compound □Suct.Press □Disch.Press |  |  |  | Coupling | Set(S)
38 | □Collar or Plug for Drain & Air Vent. |  |  |  |  | Coupling Rubber | Set(S)
39 | □Sealing Flushing Pipe |  | □ Cooling Piping |  |  | Name Plate | Set(S)
40 |  | Maker | N.E.K | Model & Size | Φ 18 |  | Set(S)
41 | Mechanical Seal | Type | EA103-18 | Cooler | □Yes, ■No | WEIGHT
42 | [5 empty] | Pump / Bed | Kg
43 | □ Companion Flange |  |  |  |  | Driver | Kg
44 | □ Special Tools |  |  |  |  | Total Wt. | 22 Kg

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
TYPE |  | AGRICULTURAL PUMP
MODEL |  | PU-S990M
SERVICE
SCALE:N/S
OUTLINE DRAWING
of PU TYPE
150

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO. | PARTS NAME | MATERIALS |  |  |  |  | Q'ty(EA)
|  | KS | ASTM | DIN
1 | CASING | PP | - | - |  |  | 1
2 | MOTOR | - | - | - |  |  | 1
3 | BERAING | 6305ZZ | - | - |  |  | 1
4 | BERAING | 6202ZZ | - | - |  |  | 1
5 | END BRACKET(A) | GC150 | - | - |  |  | 1
6 | END BRACKET(B) | GC150 |  |  |  |  | 1
7 | Mechanical Seal | NBR+CARBON+CERAMIC | - | - |  |  | 1
8 | IMPELLER | STS304 | - | - |  |  | 1
9 | PLATE | STS304 | - | - |  |  | 1
10 | DISCHARGE FLANGE | PP | - | - |  |  | 1
11 | SUCTION FLANGE | PP | - | - |  |  | 1
12 | BACK CASING | PP | - | - |  |  | 1
13 | CHECK VALVE | NBR510 | - | - |  |  | 1
14 | GUIDE VANE | SPS | - | - |  |  | 1
15 | BASE PLATE | HDPE | - | - |  |  | 1
16 | TERMINAL BOX | ABS | - | - |  |  | 1
|  |  |  | TYPE |  | AGRICULTURAL PUMP
|  |  |  | MODEL |  | PU-S990M
SERVICE
SCALE:N/S
SECTIONAL DRAWING
of PU TYPE
11
10
3
16
4
15
7
12
8
14
1
13
2
5
6
9

## Test Report
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 120 | 166 | 202 | 236 | 273 | 295 | 307
Dis. Head | (m) | 17.4 | 15 | 13 | 11 | 9 | 6 | 3 | 0.6
Suc. Head | (m) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Speed Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Head | (m) | 23.4 | 21 | 19 | 17 | 15 | 12 | 9 | 6.6
Water Power | (㎾) | 0 | 0.41076 | 0.5141 | 0.55974 | 0.57702 | 0.53399 | 0.43277 | 0.33027
Shaft Power | (㎾) | 0.67968 | 0.90985 | 1.0075 | 1.0672 | 1.1152 | 1.1501 | 1.1439 | 1.1067
Pump Eff. | (%) | 0 | 45.1459 | 51.0275 | 52.4508 | 51.7402 | 46.4297 | 37.8324 | 29.8428
Speed | (rpm) | 3527 | 3488 | 3472 | 3460 | 3450 | 3447 | 3447 | 3455
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 3.96 | 5.38 | 5.92 | 6.31 | 6.58 | 6.74 | 6.71 | 6.48
Motor Input | (㎾) | 0.877 | 1.174 | 1.3 | 1.377 | 1.439 | 1.484 | 1.476 | 1.428
Motor Eff. | (%) | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 280 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 1.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 9 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 | 50 | 50
Efficiency | 40 | (%) | Volt. (V) | 220 | Current(A) |  | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia | 50 | (mm) | Eff. (%) | 77.5 | Maker | WILO | Turbin | 20 | 10
Item No. |  |  | Serial No. |  | Inspector | K.I.H | Run (Hr) | B/R (℃) | Test Date
Model | PU-S990M |  | Customer |  |  |  | 1
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification