## Datasheet(PUF-1700I)
PUMP DATA SHEET
| Model | PUF-1700I | Title |  |  | Sheet No.
1 | Customer |  |  | Agent No.
2 | Location |  |  | Date Issued
3 | Item No. |  |  | Plant Name
4 | Service |  |  | Quantity |  | Location | ■In, □Out
5 | OPERATING CONDITION
6 | Liquid |  | Flow | 350 | ℓ/min | NPSHav | mAq
7 | Pumping Temp | AMB. ℃ | Suct.Head | 0 | m | Concentration | %
8 | Sp. Gr. @P.T | 1 | Disch.Head | 0 | m | Solid
9 | Vap. Press @P.T | Kg/㎠A | Total Head | 0 | m | Corros.or Erros
10 | Visc @P.T | Cp
11 | [5 empty] | MATERIALS
12 | ■ Horizontal | □ Vertical | Efficiency | 30 | % | (Parts' Name) | Symbol(KS)
13 | Number of Stages | 1 Stage | Rated Power | 2400 | W | Impeller | C3771BD
14 | Speed | 3400 | NPSHre |  | mAq | Shaft | SM20C+STS316
15 | Rotation | □ CW, ■ CCW | Column Head |  | m | Casing | BC1
16 | Flange | Size(Dia) | Rating | Face | Position | FILTER CASE | BC1
17 | Suction | 40mm |  | ■ FF, □ RF | □End □Top ■Side | HANDLE | BC1
18 | Discharge | 40mm |  | ■ FF, □ RF | ■Top, □Side | PILTER | PP
19 | Impeller Type | Semi Open | ■Single Suct. | □Double Suct. | HYDROSTATIC
20 | Flow Direction | ■Radial | □ Mixed | □ Axial | Casing | 3 Kg/㎠ | 3 Min.
21 | Shaft Seal | □ G/Packing | ■ M/Seal
22 | Shaft Sleeve | □Yes, □No
23 | Mounting | □ Foot | □ Centerline | □ Bracket | TESTING
24 | Lubrication Type | □ Grease | □ Oil Bath |  | (Items) |  | (witness)
25 | Cooling | □ Stuff.Box | □B/R Housing | □ No. Cooling | Run Perform. | ■ Yes □ No | □Yes □No
26 | Radial Bearings | 6204ZZ | Thrust Bearing | 6305ZZ | Hydrostatic | ■ Yes □ No | □Yes □No
27 | PUMP DRIVER |  |  |  |  | SPARE PARTS
28 | Motor | V/Phase/Hz | 220/380 | 3 | 60 | Impeller | Set(S)
29 | Maker | WILO Pumps Ltd. |  |  |  | Shaft | Set(S)
30 | Type | INDUCTION MOTOR |  |  |  | Shaft Sleeve | Set(S)
31 | Power | 2200W |  |  |  | Casing Ring | Set(S)
32 | Pole & Speed | 2 p 3400 rpm | Insulation Class | ■ B | □ E | Bearing(R+T) | Set(S)
33 | ACCESSORIES |  |  |  |  | Bearing(Journal) | Set(S)
34 | □Base Plate | □ Cast Iron | □Steel Plate |  | □ Drain Rim | M/Seal | Set(S)
35 | □Foundation Bolts & Nuts |  |  |  |  | Casing Gasket | Set(S)
36 | Coupling | □ Sun Flex | □ WOODS | □ Grid | □Coupling Guard | Oil Seal | Set(S)
37 | □Press. Gauge | □Suct.Vacuum □Suct.Compound □Suct.Press □Disch.Press |  |  |  | Coupling | Set(S)
38 | □Collar or Plug for Drain & Air Vent. |  |  |  |  | Coupling Rubber | Set(S)
39 | □Sealing Flushing Pipe |  | □ Cooling Piping |  |  | Name Plate | Set(S)
40 |  | Maker | N.E.K | Model & Size | Φ 18 |  | Set(S)
41 | Mechanical Seal | Type | EA103-18 | Cooler | □Yes, ■No | WEIGHT
42 | [5 empty] | Pump / Bed | Kg
43 | □ Companion Flange |  |  |  |  | Driver | Kg
44 | □ Special Tools |  |  |  |  | Total Wt. | 38 Kg

## Outline Drawing(PUF-1700i)
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
PUMP | CAPACITY | ℓ/min | 350 |  | MOTOR | OUTPUT |  |  |  | W | 1700
| TOTAL HEAD | m | 0 |  |  | VOLTAGE |  |  |  | V | 220
| SUCTION BORE | mm | Ø | 40 |  | FREQUENCY |  |  |  | Hz | 60
| DISCHARGE BORE | mm | Ø | 40 |  | No. OF REVOLUTION |  |  |  | r.p.m | 3400
| LIQUID | WATER |  |  |  | TYPE |  |  |  | THREE PHASE INDUCTION
| MAKER | WILO Pumps Ltd. |  |  |  | MAKER |  |  |  | WILO Pumps Ltd.
[7 empty] | TYPE |  | FILTER PUMP
[7 empty] | MODEL |  | PUF-1700i
SERVICE
SCALE:N/S
OUTLINE DRAWING
of PUF TYPE

## Sectional Drawing(PUF-1700i)
Sheet No.
CUSTOMER
ITEM No.
DATE
NO. | PARTS NAME | MATERIALS |  |  |  |  | Q'ty(EA)
|  | KS | ASTM | DIN
1 | CASING | BC1 | - | - |  |  | 1
2 | MOTOR | - | - | - |  |  | 1
3 | BERAING | 6305ZZ | - | - |  |  | 1
4 | BERAING | 6204ZZ | - | - |  |  | 1
5 | END BRACKET(A) | GC150 | class No.25 | GG15 |  |  | 1
6 | END BRACKET(B) | GC150 | class No.25 | GG15 |  |  | 1
7 | Mechanical Seal | NBR+CARBON+CERAMIC | - | - |  |  | 1
8 | IMPELLER | C3771BD | - | - |  |  | 1
9 | FILTER CASE | BC1 | - | - |  |  | 1
10 | FILTER COVER | BC1 | - | - |  |  | 1
11 | HANDLE | BC1+STS | - | - |  |  | 1
12 | FILTER | PP | - | - |  |  | 1
|  |  |  | TYPE |  | FILTER PUMP
|  |  |  | MODEL |  | PUF-1700i
SERVICE
SCALE:N/S
SECTIONAL DRAWING
of PUF TYPE
1
2
3
4
6
5
7
8
9
12
11
10

## Test Report(PUF-1700I)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 133.8 | 218 | 241 | 280 | 316.5 | 352 | 376
Dis. Head | (m) | 31.2 | 26 | 20 | 18 | 14 | 10 | 6 | 3
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Head | (m) | 31.2 | 26 | 20 | 18 | 14 | 10 | 6 | 3
Water Power | (㎾) | 0 | 0.56704 | 0.71068 | 0.70709 | 0.63896 | 0.51589 | 0.34426 | 0.18386
Shaft Power | (㎾) | 1.271 | 1.4539 | 1.5942 | 1.626 | 1.6624 | 1.7189 | 1.8096 | 1.6624
Pump Eff. | (%) | 0 | 39.0016 | 44.5798 | 43.4881 | 38.4366 | 30.0122 | 19.0236 | 11.0603
Speed | (rpm) | 3511 | 3491 | 3476 | 3474 | 3470 | 3468 | 3450 | 3445
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 5.75 | 6.26 | 6.75 | 6.8 | 6.9 | 7.08 | 7.37 | 7.56
Motor Input | (㎾) | 1.64 | 1.876 | 2.057 | 2.098 | 2.145 | 2.218 | 2.335 | 2.145
Motor Eff. | (%) | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 350 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 1.7 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 0 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 | 40 | 40
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) |  | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 77.5 | Maker | WILO | Turbin | 20 | 10
Item No. |  |  | Serial No. |  | Inspector | K.I.H | Run (Hr) | B/R (℃) | Test Date
Model | PUF-1700i |  | Customer |  |  |  | 1
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification