## Datasheet
PUMP DATA SHEET
| Model | PUN-350M | Title |  |  | Sheet No.
1 | Customer |  |  | Agent No.
2 | Location |  |  | Date Issued
3 | Item No. |  |  | Plant Name
4 | Service |  |  | Quantity |  | Location | ■In, □Out
5 | OPERATING CONDITION
6 | Liquid |  | Max. Flow | 90 | ℓ/min (Ht=0.5m) | NPSHav | mAq
7 | Pumping Temp | AMB. ℃ | Suct.Head | 0 | m | Concentration | %
8 | Sp. Gr. @P.T | 1 | Max.Dis.Press | 21 | m | Solid
9 | Vap. Press @P.T | Kg/㎠A | Total Head | 21 | m | Corros.or Erros
10 | Visc @P.T | Cp
11 | [5 empty] | MATERIALS
12 | ■ Horizontal | □ Vertical | Efficiency | 35 | % | (Parts' Name) | Symbol(KS)
13 | Number of Stages | 1 Stage | Rated Power | 350 | W | Impeller | Noryl
14 | Speed | 3400 | NPSHre |  | mAq | Shaft | STS410
15 | Rotation | □ CW, ■ CCW | Column Head |  | m | Casing | GC200
16 | Flange | Size(Dia) | Rating | Face | Position
17 | Suction | 25mm |  | ■ FF, □ RF | ■End □Top □Side
18 | Discharge | 25mm |  | ■ FF, □ RF | ■Top, □Side
19 | Impeller Type | Semi open | ■Single Suct. | □Double Suct. | HYDROSTATIC
20 | Flow Direction | ■ Radial | □ Mixed | □ Axial | Casing | 3 Kg/㎠ | 3 Min.
21 | Shaft Seal | □ G/Packing | ■ M/Seal
22 | Shaft Sleeve | □Yes, □No
23 | Mounting | □ Foot | □ Centerline | □ Bracket | TESTING
24 | Lubrication Type | □ Grease | □ Oil Bath |  | (Items) |  | (witness)
25 | Cooling | □ Stuff.Box | □B/R Housing | □ No. Cooling | Run Perform. | ■ Yes □ No | □Yes □No
26 | Radial Bearings | 6201ZZ | Thrust Bearing | 6201ZZ | Hydrostatic | ■ Yes □ No | □Yes □No
27 | PUMP DRIVER |  |  |  |  | SPARE PARTS
28 | Motor | V/Phase/Hz | 220 | 1 | 60 | Impeller | Set(S)
29 | Maker | WILO Pumps Ltd. |  |  |  | Shaft | Set(S)
30 | Type | INDUCTION MOTOR |  |  |  | Shaft Sleeve | Set(S)
31 | Power | 350W |  |  |  | Casing Ring | Set(S)
32 | Pole & Speed | 2 p 3400 rpm | Insulation Class | ■ B | □ E | Bearing(R+T) | Set(S)
33 | ACCESSORIES |  |  |  |  | Bearing(Journal) | Set(S)
34 | □Base Plate | □ Cast Iron | □Steel Plate |  | □ Drain Rim | M/Seal | Set(S)
35 | □Foundation Bolts & Nuts |  |  |  |  | Casing Gasket | Set(S)
36 | Coupling | □ Sun Flex | □ WOODS | □ Grid | □Coupling Guard | Oil Seal | Set(S)
37 | □Press. Gauge | □Suct.Vacuum □Suct.Compound □Suct.Press □Disch.Press |  |  |  | Coupling | Set(S)
38 | □Collar or Plug for Drain & Air Vent. |  |  |  |  | Coupling Rubber | Set(S)
39 | □Sealing Flushing Pipe |  | □ Cooling Piping |  |  | Name Plate | Set(S)
40 |  | Maker | N.E.K | Model & Size | Φ 12 |  | Set(S)
41 | Mechanical Seal | Type | EA104-12 | Cooler | □Yes, ■No | WEIGHT
42 | [5 empty] | Pump / Bed | Kg
43 | □ Companion Flange |  |  |  |  | Driver | Kg
44 | □ Special Tools |  |  |  |  | Total Wt. | 7.5

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
TYPE |  | AGRICULTURAL PUMP
MODEL |  | PUN-350M
SERVICE
SCALE:N/S
OUTLINE DRAWING
of PUN TYPE

## Sectional Drawing)
Sheet No.
CUSTOMER
ITEM No.
DATE
NO. | PARTS NAME | MATERIALS |  |  |  |  | Q'ty(EA)
|  | KS | ASTM | DIN
1 | CASING | GC200 |  |  |  |  | 1
2 | MOTOR | - |  |  |  |  | 1
3 | CAPACITOR COVER | P.P |  |  |  |  | 1
4 | END BRACKET(A) | GC150 |  |  |  |  | 1
5 | END BRACKET(B) | ALDC8 |  |  |  |  | 1
6 | Mechanical Seal | SIC/CARBON |  |  |  |  | 1
7 | NUT | [5 empty] | 1
8 | DRAIN SCREW | MSWR3 |  |  |  |  | 1
9 | IMPELLER | NORYL |  |  |  |  | 1
10 | FAN | PBT |  |  |  |  | 1
11 | FAN COVER | ABS |  |  |  |  | 1
12 | SUPPORTER | PBT |  |  |  |  | 1
|  |  |  | TYPE |  | AGRICULTURAL PUMP
|  |  |  | MODEL |  | PUN-350M
SERVICE
SCALE:N/S
SECTIONAL DRAWING
of PUN TYPE

## Test Report
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 43.9 | 63.6 | 72.8 | 89.4 | 95.7 | 109.5 | 113.2
Dis. Head | (m) | 22.5 | 18 | 14 | 12 | 8 | 6 | 2 | 0.8
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Head | (m) | 22.5 | 18 | 14 | 12 | 8 | 6 | 2 | 0.8
Water Power | (㎾) | 0 | 0.1288 | 0.14514 | 0.1424 | 0.11658 | 0.093595 | 0.035697 | 0.014761
Shaft Power | (㎾) | 0.2336 | 0.32384 | 0.34112 | 0.3456 | 0.3456 | 0.34304 | 0.3328 | 0.3296
Pump Eff. | (%) | 0 | 39.7735 | 42.5467 | 41.2028 | 33.7319 | 27.2839 | 10.7263 | 4.4785
Speed | (rpm) | 3508 | 3443 | 3422 | 3416 | 3415 | 3416 | 3424 | 3426
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 1.67 | 2.25 | 2.4 | 2.43 | 2.42 | 2.4 | 2.32 | 2.3
Motor Input | (㎾) | 0.365 | 0.506 | 0.533 | 0.54 | 0.54 | 0.536 | 0.52 | 0.515
Motor Eff. | (%) | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 90 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.35 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 0.5 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 | 25 | 25
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) |  | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 64 | Maker | WILO | Turbin | 14 | 12
Item No. |  |  | Serial No. |  | Inspector | K.I.H | Run (Hr) | B/R (℃) | Test Date
Model | PUN-350M |  | Customer |  |  |  | 1
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 294.288 | 294.288 | 294.288 | 294.288 | 294.288 | 294.288 | 294.288 | 294.288
Suc. Head | m | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Suc. Head | m | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Vacuum | mmhg | 294.288 | 294.288 | 294.288 | 294.288 | 294.288 | 294.288 | 294.288 | 294.288
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification