## Datasheet
PUMP DATA SHEET
| Model | PUN-600M | Title |  |  | Sheet No.
1 | Customer |  |  | Agent No.
2 | Location |  |  | Date Issued
3 | Item No. |  |  | Plant Name
4 | Service |  |  | Quantity |  | Location | ■In, □Out
5 | OPERATING CONDITION
6 | Liquid |  | Flow | 85 | ℓ/min (Ht=0.5m 일때) | NPSHav | mAq
7 | Pumping Temp | AMB. ℃ | Suct.Head | 0 | m | Concentration | %
8 | Sp. Gr. @P.T | 1 | Disch.Press | 28 | m(Max.) | Solid
9 | Vap. Press @P.T | Kg/㎠A | Total Head | 28 | m | Corros.or Erros
10 | Visc @P.T | Cp
11 | [5 empty] | MATERIALS
12 | ■ Horizontal | □ Vertical | Efficiency | 25 | % | (Parts' Name) | Symbol(KS)
13 | Number of Stages | 1 Stage | Rated Power | 600 | W | Impeller | NORYL
14 | Speed | 3400 rpm | NPSHre |  | mAq | Valve | NORYL
15 | Rotation | □ CW, ■ CCW | Column Head |  | m | Shaft | STS410
16 | Bore | Size(Dia) | Rating | Face | Position | Casing | Coated GC200
17 | Suction | 32mm(1 1/4") |  | □ FF, □ RF | ■End □Top □Side | Terminal Box | ABS
18 | Discharge | 32mm(1 1/4") |  | □ FF, □ RF | ■Top, □Side
19 | Impeller Type | CLOSED | ■Single Suct. | □Double Suct. | HYDROSTATIC
20 | Flow Direction | ■ Radial | □ Mixed | □ Axial | Casing | 5 Kg/㎠ | 3 Min.
21 | Shaft Seal | □ G/Packing | ■ M/Seal
22 | Shaft Sleeve | □Yes, □No
23 | Mounting | □ Foot | □ Centerline | □ Bracket | TESTING
24 | Lubrication Type | □ Grease | □ Oil Bath |  | (Items) |  | (witness)
25 | Cooling | □ Stuff.Box | □B/R Housing | □ No. Cooling | Run Perform. | ■ Yes □ No | □Yes □No
26 | Radial Bearings | 6302zz | Thrust Bearing | 6202zz | Hydrostatic | ■ Yes □ No | □Yes □No
27 | PUMP DRIVER |  |  |  |  | SPARE PARTS
28 | Motor | V/Phase/Hz | 220 | 1 | 60 | Impeller | Set(S)
29 | Maker | WILO Pumps Ltd. |  |  |  | Shaft | Set(S)
30 | Type | INDUCTION MOTOR |  |  |  | Shaft Sleeve | Set(S)
31 | Power | 600W |  |  |  | Casing Ring | Set(S)
32 | Pole & Speed | 2 p 3400 rpm | Insulation Class | ■ F | □ E | Bearing(R+T) | Set(S)
33 | ACCESSORIES |  |  |  |  | Bearing(Journal) | Set(S)
34 | □Base Plate | □ Cast Iron | □Steel Plate |  | □ Drain Rim | M/Seal | Set(S)
35 | □Foundation Bolts & Nuts |  |  |  |  | Casing Gasket | Set(S)
36 | Coupling | □ Sun Flex | □ WOODS | □ Grid | □Coupling Guard | Oil Seal | Set(S)
37 | □Press. Gauge | □Suct.Vacuum □Suct.Compound □Suct.Press □Disch.Press |  |  |  | Coupling | Set(S)
38 | □Collar or Plug for Drain & Air Vent. |  |  |  |  | Coupling Rubber | Set(S)
39 | □Sealing Flushing Pipe |  | □ Cooling Piping |  |  | Name Plate | Set(S)
40 |  | Maker | N.E.K | Model & Size | Φ 15 |  | Set(S)
41 | Mechanical Seal | Type | EA104-15 | Cooler | □Yes, ■No | WEIGHT
42 | [5 empty] | Pump / Bed | 3.6 Kg
43 | □ Companion Flange |  |  |  |  | Driver | 7.8 Kg
44 | □ Special Tools |  |  |  |  | Total Wt. | 11.4 Kg

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
TYPE |  | AGRICULTURAL PUMP
MODEL |  | PUN-600M
SERVICE
SCALE:N/S
OUTLINE DRAWING
of PUN TYPE

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO. | PARTS NAME | MATERIALS |  |  |  |  | Q'ty(EA)
|  | KS | ASTM | DIN
1 | Motor | - | - | - |  |  | 1
2 | T/Base &Cover | ABS | - | - |  |  | 1
3 | Impeller | NORYL | - | - |  |  | 1
4 | Mechanical Seal | NBR+CARBON+CERAMIC | - | - |  |  | 1
5 | Casing | GC200 | - | - |  |  | 1
6 | Motor Support | PBT | - | - |  |  | 1
7 | Fan | P.E | - | - |  |  | 1
8 | Fan Cover | P.P | - | - |  |  | 1
|  |  |  | TYPE |  | AGRICULTURAL PUMP
|  |  |  | MODEL |  | PUN-600M
SERVICE
SCALE:N/S
SECTIONAL DRAWING
of PU TYPE

## Test Report
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 39.8 | 67.8 | 87.4 | 98 | 107 | 114.2
Dis. Head | (m) | 29.5 | 25 | 20 | 15 | 10 | 5 | 1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Head | (m) | 29.5 | 25 | 20 | 15 | 10 | 5 | 1
Water Power | (㎾) | 0 | 0.16218 | 0.22103 | 0.21369 | 0.15974 | 0.087205 | 0.018615
Shaft Power | (㎾) | 0.4644 | 0.57024 | 0.63576 | 0.67104 | 0.6876 | 0.70056 | 0.70848
Pump Eff. | (%) | 0 | 28.4415 | 34.7659 | 31.845 | 23.2315 | 12.4479 | 2.6274
Speed | (rpm) | 3455 | 3407 | 3376 | 3356 | 3340 | 3337 | 3330
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 3.24 | 3.81 | 4.19 | 4.39 | 4.49 | 4.58 | 4.62
Motor Input | (㎾) | 0.645 | 0.792 | 0.883 | 0.932 | 0.955 | 0.973 | 0.984
Motor Eff. | (%) | 72 | 72 | 72 | 72 | 72 | 72 | 72
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 65 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.6 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 20 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 | 32 | 32
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 4.8 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 72 | Maker | WILO | Turbin | 28 | 24
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PUN-600M |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification