## Datasheet
PUMP DATA SHEET
| Model | PW-2200UA | Title |  |  | Sheet No.
1 | Customer |  |  | Agent No.
2 | Location |  |  | Date Issued
3 | Item No. |  |  | Plant Name
4 | Service |  |  | Quantity |  | Location | ■In, □Out
5 | OPERATING CONDITION
6 | Liquid | Water | Flow | 45 | ℓ/min at Ht=40m | NPSHav | mAq
7 | Pumping Temp | 0~40 ℃ | Suct.Head | 8 | m | Concentration | %
8 | Sp. Gr. @P.T | 1 | Disch.Press | 45 | m | Solid
9 | Vap. Press @P.T | Kg/㎠A | Total Head | 53 | m | Corros.or Erros
10 | Visc @P.T | Cp
11 | PERFORMANCE AND CONSTRUCTIONS |  |  |  |  | MATERIALS
12 | ■ Horizontal | □ Vertical | Efficiency | 20 | % | (Parts' Name) | Symbol(KS)
13 | Number of Stages | 1 Stage | Rated Power | 2200 | W | Impeller | C3771BD
14 | Speed | 3400 rpm | NPSHre |  | mAq | Impeller Cover | GC150/C3771BD
15 | Rotation | □ CW, ■ CCW | Column Head |  | m | Shaft | STS410
16 | Flange | Size(Dia) | Rating | Face | Position | Casing | GC150
17 | Suction | 40mm |  | ■ FF, □ RF | □End □Top ■Side | Flange | GC200
18 | Discharge | 40mm |  | ■ FF, □ RF | □Top, ■Side
19 | Impeller Type | Wetco Impeller | ■Single Suct. | □Double Suct. | HYDROSTATIC
20 | Flow Direction | ■ Radial | □ Mixed | □ Axial | Casing | 9 Kg/㎠ | 3 Min.
21 | Shaft Seal | □ G/Packing | ■ M/Seal |  | Pressure Tank | 10 Kg/㎠ | 3 Min.
22 | Shaft Sleeve | □Yes, ■No
23 | Mounting | ■ Foot | □ Centerline | □ Bracket | TESTING
24 | Lubrication Type | ■ Grease | □ Oil Bath |  | (Items) | (self test) | (witness)
25 | Cooling | □ Stuff.Box | □B/R Housing | ■ No. Cooling | Run Perform. | ■ Yes □ No | □Yes ■No
26 | Radial Bearings | 6205ZZ | Thrust Bearing | 6204ZZ | Hydrostatic | ■ Yes □ No | □Yes ■No
27 | PUMP DRIVER |  |  |  |  | SPARE PARTS
28 | Motor | V/Phase/Hz | 380 | 3 | 60 | Impeller | Set(S)
29 | Maker | WILO |  |  |  | Shaft | Set(S)
30 | Type | TEFC |  |  |  | Shaft Sleeve | Set(S)
31 | Power | 2200W |  |  |  | Casing Ring | Set(S)
32 | Pole & Speed | 2 p 3400 rpm | Insulation | ■ B | □ E | Bearing(R+T) | Set(S)
33 | ACCESSORIES |  |  |  |  | Bearing(Journal) | Set(S)
34 | ■Base Plate | □ Cast Iron | □ Plastic | ■ Steel Plate | □ Drain Rim | M/Seal | Set(S)
35 | □Foundation Bolts & Nuts |  |  |  |  | Casing Gasket | Set(S)
36 | Coupling | □ Sun Flex | □ WOODS | □ Grid | ■No | Oil Seal | Set(S)
37 | ■Press. Gauge | □Suct.Vacuum □Suct.Compound □Suct.Press ■Disch.Press □No |  |  |  | Coupling | Set(S)
38 | ■Plug for Priming & Screw for Drain |  |  |  |  | Coupling Rubber | Set(S)
39 | □Sealing Flushing Pipe |  | □ Cooling Piping | ■No |  | Name Plate | Set(S)
40 |  | Maker | N.E.K | Model & Size | Φ 18 | Spring | Set(S)
41 | Mechanical Seal | Type | EA103-18 | Cooler | □Yes, ■No | WEIGHT
42 | [5 empty] | Pump / Bed | Kg
43 | ■ Companion Flange |  |  |  |  | Driver | Kg
44 | □ Special Tools |  |  |  |  | Total Wt. | 52 Kg

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
PUMP | CAPACITY | ℓ/min | 45 |  | MOTOR | OUTPUT |  |  |  | W | 2200
| TOTAL HEAD | m | 53 |  |  | VOLTAGE |  |  |  | V | 220/380
| SUCTION FLANGE | mm | Ø | 40 |  | FREQUENCY |  |  |  | Hz | 60
| DISCHARGE FLANGE | mm | Ø | 40 |  | No. OF REVOLUTION |  |  |  | r.p.m | 3400 | ``
| LIQUID | WATER |  |  |  | TYPE |  |  |  | 3 PHASE INDUCTION
| MAKER | WILO |  |  |  | MAKER |  |  |  | WILO
[7 empty] | TYPE |  | WESTCO PUMP
[7 empty] | MODEL |  | PW-2200UA
SERVICE
SCALE : N/S
OUTLINE DRAWING
of PW TYPE

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO. | PARTS NAME | MATERIALS |  |  |  | Q'ty(EA)
1 | MOTOR | ALDC Frame |  |  |  | 1
2 | CAPACITOR COVER | SPCC |  |  |  | 1
3 | IMPELLER | C3771BD |  |  |  | 1
4 | CASING | GC150 |  |  |  | 1
5 | DISCHARGE FLANGE | GC200 |  |  |  | 1
6 | GASKET | NBR |  |  |  | 1
7 | SUCTION FLANGE | C3771BD |  |  |  | 1
8 | CHECK VALVE | PBT |  |  |  | 1
9 | FLEXIBLE HOSE | - |  |  |  | 1
10 | MECHANICAL SEAL | CARBON+CERAMIC |  |  |  | 1
11 | PRESSURE TANK | SPCC/NBR/STS |  |  |  | 1
12 | BASE PLATE | SPCC |  |  |  | 1
13 | CONTROL BOX | - |  |  |  | 1
14 | PRESSURE GAUGE | - |  |  |  | 1
15 | PRESSURE SWITCH | - |  |  |  | 1
|  |  | TYPE |  | WESTCO PUMP
|  |  | MODEL |  | PW-2200UA
SERVICE
SCALE:N/S
SECTIONAL DRAWING
of PW TYPE

## Test Report
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 17.2 | 28.5 | 40.5 | 49.9 | 52.5 | 58.2
Dis. Head | (m) | 93 | 80 | 70 | 60 | 50 | 46 | 20
Suc. Head | (m) | 6 | 6 | 6 | 6 | 6 | 6 | 6
Speed Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Head | (m) | 99 | 86 | 76 | 66 | 56 | 52 | 26
Water Power | (㎾) | 0 | 0.24111 | 0.35306 | 0.4357 | 0.45549 | 0.44499 | 0.24665
Shaft Power | (㎾) | 2.9019 | 2.6435 | 2.4157 | 2.2245 | 2.0069 | 1.9252 | 1.3098
Pump Eff. | (%) | 0 | 9.1208 | 14.6151 | 19.5868 | 22.6966 | 23.1134 | 18.8305
Speed | (rpm) | 3390 | 3399 | 3414 | 3430 | 3449 | 3454 | 3510
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 5.86 | 5.4 | 4.96 | 4.61 | 4.22 | 4.08 | 3.05
Motor Input | (㎾) | 3.414 | 3.11 | 2.842 | 2.617 | 2.361 | 2.265 | 1.541
Motor Eff. | (%) | 85 | 85 | 85 | 85 | 85 | 85 | 85
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 45 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 52 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 | 40 | 40
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 6 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 85 | Maker | WILO | Electirc | 11 | 19
Item No. |  |  | Serial No. | 표준품 | Inspector | S.W.H | Run (Hr) | B/R (℃) | Test Date
Model | PW-2200UA |  | Customer |  |  |  | 1
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Data (hidden)
No. | Model | Capa.(ℓ/min.) | Head(m) | Power Supply | Output | Disharge | Pole | RPM | Impeller Type | Suction | Casing Mat'l | Impeller Mat'l | Shaft Mat'l | Flange Mat'l | Capa1 | Capa2 | Capa3 | Capa4 | Capa5 | Head1 | Head2 | Head3 | Head4 | Head5 | SP1 | SP2 | SP3 | SP4 | SP5 | Eff1 | Eff2 | Eff3 | Eff4 | Eff5 | 380V Amp.
1 | PU-756M | 200(at Ht 6m) | 35 | 1Phase 220V 60Hz | 750 | Clean Water | 2 | 3400 | □ Closed ■ Semi-Open □ Open | 50(2") | GC150 | C3771BD | STS410 | GC200 | 0 | 107.7 | 172 | 227.5 | 233 | 21.7 | 18 | 14 | 8 | 6.5 | 0.35 | 0.51 | 0.59 | 0.63 | 0.62 | 0 | 61.83 | 66.51 | 47.21 | 39.59 | 8
2 | PW-K130MA | 200(at Ht 6m) | 35 | 1Phase 220V 60Hz | 750 | Clean Water | 2 | 3400 | □ Closed ■ Semi-Open □ Open | 50(2") | GC150 | C3771BD | STS410 | GC200 | 0 | 107.7 | 172 | 227.5 | 233 | 21.7 | 18 | 14 | 8 | 6.5 | 0.35 | 0.51 | 0.59 | 0.63 | 0.62 | 0 | 61.83 | 66.51 | 47.21 | 39.59 | 8
3 | PW-409MA | 32(at Ht 12m) | 30 | 1Phase 220V 60Hz | 400 | Clean Water | 2 | 3400 | □ Closed ■ Westo □ Open | 30(1 1/4") | GC150 | C3771BD | STS410 | GC200 | 0 | 8.1 | 16.7 | 28.5 | 38 | 55 | 46 | 36 | 21 | 9 | 0.6 | 0.55 | 0.47 | 0.37 | 0.3 | 0 | 11.12 | 20.82 | 26.38 | 18.59 | 8
4 | PW-405M | 40(at Ht 12m) | 36 | 1Phase 220V 60Hz | 400 | Clean Water | 2 | 3400 | □ Closed ■ Westo □ Open | 30(1 1/4") | GC150 | C3771BD | STS410 | GC200 | 0 | 10 | 31 | 41 | 46 | 53 | 46 | 26 | 16 | 9.5 | 0.73 | 0.65 | 0.46 | 0.39 | 0.34 | 0 | 11.48 | 28.68 | 27.55 | 20.94 | 8
5 | PW-804MA | 45(at Ht 12m) | 33 | 1Phase 220V 60Hz | 750 | Clean Water | 2 | 3400 | □ Closed ■ Westo □ Open | 40(1 1/2") | GC150 | C3771BD | STS410 | GC200 | 0 | 15 | 32 | 46 | 50 | 74 | 56 | 34 | 16 | 12 | 0.99 | 0.85 | 0.67 | 0.54 | 0.52 | 0 | 16.14 | 26.51 | 22.15 | 18.88 | 8