## Datasheet
PUMP DATA SHEET
| Model | PW-350NMA | Title |  |  | Sheet No.
1 | Customer |  |  | Agent No.
2 | Location |  |  | Date Issued
3 | Item No. |  |  | Plant Name
4 | Service |  |  | Quantity |  | Location | ■In, □Out
5 | OPERATING CONDITION
6 | Liquid | Water | Flow | 1.38 | ㎥/hr at Ht=15m | NPSHav | mAq
7 | Pumping Temp | 0~40 ℃ | Suct.Head | 6 | m | Concentration | %
8 | Sp. Gr. @P.T | 1 | Disch.Press | 9 | m | Solid
9 | Vap. Press @P.T | Kg/㎠A | Total Head | 15 | m | Corros.or Erros
10 | Visc @P.T | Cp
11 | PERFORMANCE AND CONSTRUCTIONS |  |  |  |  | MATERIALS
12 | ■ Horizontal | □ Vertical | Efficiency | 20 | % | (Parts' Name) | Symbol(KS)
13 | Number of Stages | 1 Stage | Rated Power | 350 | W | Impeller | C3771BD
14 | Speed | 3400 rpm | NPSHre |  | mAq | Impeller Cover | PBT(GP-2300)
15 | Rotation | □ CW, ■ CCW | Column Head |  | m | Shaft | STS410
16 | Flange | Size(Dia) | Rating | Face | Position | Casing | GC150
17 | Suction | 25mm |  | ■ FF, □ RF | □End □Top ■Side | Flange | GC200
18 | Discharge | 25mm |  | ■ FF, □ RF | □Top, ■Side | Chamber | GC150
19 | Impeller Type | Wetco Impeller | ■Single Suct. | □Double Suct. | HYDROSTATIC
20 | Flow Direction | ■ Radial | □ Mixed | □ Axial | Casing | 6 Kg/㎠ | 3 Min.
21 | Shaft Seal | □ G/Packing | ■ M/Seal |  | Pressure Tank | 7.5 Kg/㎠ | 3 Min.
22 | Shaft Sleeve | □Yes, ■No
23 | Mounting | ■ Foot | □ Centerline | □ Bracket | TESTING
24 | Lubrication Type | ■ Grease | □ Oil Bath |  | (Items) | (self test) | (witness)
25 | Cooling | □ Stuff.Box | □B/R Housing | ■ No. Cooling | Run Perform. | ■ Yes □ No | □Yes ■No
26 | Radial Bearings | 6201ZZ | Thrust Bearing | 6201ZZ | Hydrostatic | ■ Yes □ No | □Yes ■No
27 | PUMP DRIVER |  |  |  |  | SPARE PARTS
28 | Motor | V/Phase/Hz | 220 | 1 | 60 | Impeller | Set(S)
29 | Maker | WILO PUMPS LTD. |  |  |  | Shaft | Set(S)
30 | Type | ODP |  |  |  | Shaft Sleeve | Set(S)
31 | Power | 350W |  |  |  | Casing Ring | Set(S)
32 | Pole & Speed | 2 p 3400 rpm | Insulation | ■ B | □ E | Bearing(R+T) | Set(S)
33 | ACCESSORIES |  |  |  |  | Bearing(Journal) | Set(S)
34 | ■Base Plate | □ Cast Iron | ■ Plastic | □ Steel Plate | □ Drain Rim | M/Seal | Set(S)
35 | □Foundation Bolts & Nuts |  |  |  |  | Casing Gasket | Set(S)
36 | Coupling | □ Sun Flex | □ WOODS | □ Grid | ■No | Oil Seal | Set(S)
37 | □Press. Gauge | □Suct.Vacuum □Suct.Compound □Suct.Press □Disch.Press ■No |  |  |  | Coupling | Set(S)
38 | ■Plug for Priming & Screw for Drain |  |  |  |  | Coupling Rubber | Set(S)
39 | □Sealing Flushing Pipe |  | □ Cooling Piping | ■No |  | Name Plate | Set(S)
40 |  | Maker | N.E.K | Model & Size | Φ 12 | Spring | 1 Set(S)
41 | Mechanical Seal | Type | EA103-12 | Cooler | □Yes, ■No | WEIGHT
42 | [5 empty] | Pump / Bed | Kg
43 | ■ Companion Flange |  |  |  |  | Driver | Kg
44 | □ Special Tools |  |  |  |  | Total Wt. | 19 Kg

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
TYPE |  | WESTCO PUMP
MODEL |  | PW-350NMA
SERVICE
SCALE : N/S
OUTLINE DRAWING
of PW TYPE

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO. | PARTS NAME | MATERIALS |  |  |  | Q'ty(EA)
1 | MOTOR | - |  |  |  | 1
2 | CAPACITOR COVER | 난연 ABS(AF-305F) |  |  |  | 1
3 | IMPELLER | C3771BD |  |  |  | 1
4 | CASING (BODY) | GC150 |  |  |  | 1
5 | DISCHARGE FLANGE | GC200 |  |  |  | 1
6 | FLANGE GASKET | NBR |  |  |  | 2
7 | SUCTION FLANGE | GC200 |  |  |  | 1
8 | CHECK VALVE | NBR / PBT |  |  |  | 1
9 | MECHANICAL SEAL | CARBON / CERAMIC |  |  |  | 1
10 | AIR CHARGE | - |  |  |  | 1
11 | CHAMBER | GC150 |  |  |  | 1
12 | HOPPER CAP | PBT |  |  |  | 1
13 | PRESSURE SWITCH | - |  |  |  | 1
14 | PRESSURE TANK | SCP |  |  |  | 1
15 | IMPELLER COVER | PBT |  |  |  | 1
|  |  | TYPE |  | WESTCO PUMP
|  |  | MODEL |  | PW-350NMA
SERVICE
SCALE:N/S
SECTIONAL DRAWING
of PW TYPE

## Performance Curve
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (㎥/hr) | 0 | 0.48 | 0.66 | 0.84 | 1.02 | 1.2 | 1.56 | 1.68
Dis. Head | (m) | 46.5 | 35 | 30 | 25 | 20 | 16 | 7 | 2
Suc. Head | (m) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Speed Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Head | (m) | 52.5 | 41 | 36 | 31 | 26 | 22 | 13 | 8
Water Power | (㎾) | 0 | 0.0032078 | 0.0038729 | 0.0042445 | 0.0043228 | 0.0043032 | 0.0033056 | 0.0021907
Shaft Power | (㎾) | 0.43281 | 0.36288 | 0.35469 | 0.31059 | 0.28413 | 0.26271 | 0.22491 | 0.19908
Pump Eff. | (%) | 0 | 0.88399 | 1.0919 | 1.3666 | 1.5214 | 1.638 | 1.4698 | 1.1004
Speed | (rpm) | 3314 | 3363 | 3404 | 3446 | 3477 | 3505 | 3514 | 3525
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 3.11 | 2.61 | 2.4 | 2.21 | 2.03 | 1.18 | 1.62 | 1.45
Motor Input | (㎾) | 0.687 | 0.576 | 0.563 | 0.493 | 0.451 | 0.417 | 0.357 | 0.316
Motor Eff. | (%) | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 1.38 | (㎥/hr) | Phase (Φ) | 1 | Output(㎾) | 0.35 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 15 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 | 25 | 25
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 2.3 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 63 | Maker | WILO | Electric | 22 | 18
Item No. |  |  | Serial No. | 표준품 | Inspector | S.G.S | Run (Hr) | B/R (℃) | Test Date
Model | PW-350NMA |  | Customer |  |  |  | 1
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Data (hidden)
No. | Model | Capa.(ℓ/min.) | Head(m) | Power Supply | Output | Disharge | Pole | RPM | Impeller Type | Suction | Casing Mat'l | Impeller Mat'l | Shaft Mat'l | Flange Mat'l | Capa1 | Capa2 | Capa3 | Capa4 | Capa5 | Head1 | Head2 | Head3 | Head4 | Head5 | SP1 | SP2 | SP3 | SP4 | SP5 | Eff1 | Eff2 | Eff3 | Eff4 | Eff5 | Discharge | 380V Amp.
1 | PW-K130MA | 18(at Ht 12m) | 15 | 1Phase 220V 60Hz | 125 | Clean Water | 2 | 3400 | □ Closed ■ Westo □ Open | 20(3/4") | GC150 | C3771BD | STS410 | GC200 | 0 | 6.5 | 13.2 | 21.5 | 24.4 | 44 | 36 | 26 | 12 | 6 | 0.35 | 0.28 | 0.22 | 0.16 | 0.14 | 0 | 13.73 | 25.47 | 26.05 | 16.91 | 20(3/4") | 8
2 | PW-K132M | 18(at Ht 12m) | 21 | 1Phase 220V 60Hz | 125 | Clean Water | 2 | 3400 | □ Closed ■ Westo □ Open | 20(3/4") | GC150 | C3771BD | STS410 | GC200 | 0 | 5 | 12.7 | 19 | 21.4 | 44.5 | 36 | 26 | 16 | 12 | 0.35 | 0.29 | 0.23 | 0.18 | 0.16 | 0 | 10.1 | 23.36 | 27.52 | 25.39 | 20(3/4") | 8
3 | PW-K134MA | 9(at Ht 12m) | 19 | 1Phase 220V 60Hz | 125 | Clean Water | 2 | 3400 | □ Closed ■ Westo □ Open | 15(1/2") | GC150 | C3771BD | STS410 | GC200 | 0 | 6 | 12.1 | 19.4 | 19.6 | 46.6 | 36 | 26 | 12 | 6.5 | 0.32 | 0.26 | 0.21 | 0.15 | 0.13 | 0 | 13.46 | 24.28 | 24.71 | 15.84 | 15(1/2") | 8
4 | PWS-K125MA | 18(at Ht 12m) | 10 | 1Phase 220V 60Hz | 125 | Clean Water | 2 | 3400 | □ Closed ■ Westo □ Open | 20(3/4") | GC150 | C3771BD | STS410 | GC200 | 0 | 4.8 | 15 | 20.7 | 28.4 | 35 | 28 | 18 | 12 | 4 | 0.32 | 0.27 | 0.21 | 0.18 | 0.15 | 0 | 7.97 | 20.71 | 22.57 | 12.71 | 20(3/4") | 8
5 | PW-K252MA | 25(at Ht 12m) | 24 | 1Phase 220V 60Hz | 250 | Clean Water | 2 | 3400 | □ Closed ■ Westo □ Open | 25(1") | GC150 | C3771BD | STS410 | GC200 | 0 | 9.1 | 16.5 | 26.9 | 32.2 | 54.8 | 41 | 31 | 16 | 8 | 0.5 | 0.4 | 0.34 | 0.25 | 0.21 | 0 | 15.2 | 24.85 | 28.05 | 19.8 | 25(1") | 8
6 | PW-K261M | 25(at Ht 12m) | 32 | 1Phase 220V 60Hz | 250 | Clean Water | 2 | 3400 | □ Closed ■ Westo □ Open | 25(1") | GC150 | C3771BD | STS410 | GC200 | 0 | 8.5 | 21.3 | 26.5 | 28.3 | 61 | 46 | 26 | 16 | 7.5 | 0.52 | 0.41 | 0.29 | 0.23 | 0.18 | 0 | 15.46 | 31.5 | 29.95 | 18.87 | 25(1") | 8
7 | PW-K265M | 20(at Ht 12m) | 32 | 1Phase 220V 60Hz | 250 | Clean Water | 2 | 3400 | □ Closed ■ Westo □ Open | 15(1/2") | GC150 | C3771BD | STS410 | GC200 | 0 | 2 | 8.9 | 19.9 | 20.9 | 58 | 51 | 41 | 21 | 6.8 | 0.48 | 0.44 | 0.38 | 0.26 | 0.18 | 0 | 3.79 | 15.83 | 26.43 | 13.09 | 15(1/2") | 8
8 | PW-K267M | 20(at Ht 12m) | 32 | 1Phase 220V 60Hz | 250 | Clean Water | 2 | 3400 | □ Closed ■ Westo □ Open | 15(1/2") | GC150 | C3771BD | STS410 | GC200 | 0 | 2 | 8.9 | 19.9 | 20.9 | 58 | 51 | 41 | 21 | 6.8 | 0.48 | 0.44 | 0.38 | 0.26 | 0.18 | 0 | 3.79 | 15.83 | 26.43 | 13.09 | 15(1/2") | 8
9 | PW-265M | 20(at Ht 12m) | 32 | 1Phase 220V 60Hz | 250 | Clean Water | 2 | 3400 | □ Closed ■ Westo □ Open | 15(1/2") | GC150 | C3771BD | STS410 | GC200 | 0 | 2 | 8.9 | 19.9 | 20.9 | 58 | 51 | 41 | 21 | 6.8 | 0.48 | 0.44 | 0.38 | 0.26 | 0.18 | 0 | 3.79 | 15.83 | 26.43 | 13.09 | 15(1/2") | 8
10 | PW-255MA | 25(at Ht 12m) | 24 | 1Phase 220V 60Hz | 250 | Clean Water | 2 | 3400 | □ Closed ■ Westo □ Open | 25(1") | GC150 | C3771BD | STS410 | GC200 | 0 | 4.1 | 11.7 | 21.4 | 31.8 | 54.6 | 46 | 36 | 21 | 7.8 | 0.49 | 0.43 | 0.37 | 0.28 | 0.22 | 0 | 7.18 | 18.73 | 26.33 | 18.02 | 25(1") | 8
11 | PW-256MA | 25(at Ht 12m) | 24 | 1Phase 220V 60Hz | 250 | Clean Water | 2 | 3400 | □ Closed ■ Westo □ Open | 25(1") | GC150 | C3771BD | STS410 | GC200 | 0 | 4.1 | 11.7 | 21.4 | 31.8 | 54.6 | 46 | 36 | 21 | 7.8 | 0.49 | 0.43 | 0.37 | 0.28 | 0.22 | 0 | 7.18 | 18.73 | 26.33 | 18.02 | 25(1") | 8
12 | PW-S254MA | 25(at Ht 12m) | 24 | 1Phase 220V 60Hz | 250 | Clean Water | 2 | 3400 | □ Closed ■ Westo □ Open | 25(1") | GC150 | C3771BD | STS410 | GC200 | 0 | 3.5 | 14.8 | 27.1 | 30.1 | 57 | 51 | 36 | 16 | 7.5 | 0.55 | 0.5 | 0.39 | 0.26 | 0.21 | 0 | 5.85 | 22.28 | 26.94 | 17.27 | 25(1") | 8
13 | PWS-K250MA | 25(at Ht 12m) | 19 | 1Phase 220V 60Hz | 250 | Clean Water | 2 | 3400 | □ Closed ■ Westo □ Open | 25(1") | GC150 | C3771BD | STS410 | GC200 | 0 | 8.2 | 20 | 32 | 39.5 | 40.5 | 33 | 23 | 12 | 5.2 | 0.41 | 0.35 | 0.28 | 0.21 | 0.18 | 0 | 12.56 | 26.77 | 29.77 | 19.06 | 25(1") | 8
14 | PWS-K253MA | 25(at Ht 12m) | 19 | 1Phase 220V 60Hz | 250 | Clean Water | 2 | 3400 | □ Closed ■ Westo □ Open | 25(1") | BC3 | C3771BD | STS410 | BC3 | 0 | 10 | 19.5 | 30 | 37 | 43 | 33 | 23 | 12 | 5 | 0.44 | 0.37 | 0.3 | 0.24 | 0.2 | 0 | 14.62 | 24.37 | 24.81 | 15.03 | 25(1") | 8
15 | PW-405M | 40(at Ht 12m) | 36 | 1Phase 220V 60Hz | 400 | Clean Water | 2 | 3400 | □ Closed ■ Westo □ Open | 30(1 1/4") | GC150 | C3771BD | STS410 | GC200 | 0 | 10 | 21 | 41 | 46 | 53 | 46 | 36 | 16 | 9.5 | 0.73 | 0.65 | 0.55 | 0.39 | 0.34 | 0 | 11.48 | 22.28 | 27.55 | 20.94 | 30(1 1/4") | 8
16 | PW-406MA | 40(at Ht 12m) | 26 | 1Phase 220V 60Hz | 400 | Clean Water | 2 | 3400 | □ Closed ■ Westo □ Open | 30(1 1/4") | GC150 | C3771BD | STS410 | GC200 | 0 | 4 | 21.2 | 43.2 | 45 | 48.8 | 46 | 34 | 12 | 10.1 | 0.65 | 0.63 | 0.52 | 0.35 | 0.33 | 0 | 4.74 | 22.58 | 24.08 | 22.15 | 30(1 1/4") | 8
17 | PW-409MA | 32(at Ht 12m) | 30 | 1Phase 220V 60Hz | 400 | Clean Water | 2 | 3400 | □ Closed ■ Westo □ Open | 30(1 1/4") | GC150 | C3771BD | STS410 | GC200 | 0 | 8.1 | 16.7 | 28.5 | 38 | 55 | 46 | 36 | 21 | 9 | 0.6 | 0.55 | 0.47 | 0.37 | 0.3 | 0 | 11.12 | 20.82 | 26.38 | 18.59 | 30(1 1/4") | 8
18 | PW-S406MA | 40(at Ht 12m) | 26 | 1Phase 220V 60Hz | 400 | Clean Water | 2 | 3400 | □ Closed ■ Westo □ Open | 30(1 1/4") | GC150 | C3771BD | STS410 | GC200 | 0 | 7.9 | 22.3 | 37.6 | 48.5 | 59 | 51 | 36 | 21 | 6.3 | 0.8 | 0.72 | 0.57 | 0.43 | 0.3 | 0 | 9.18 | 23.14 | 30.14 | 16.55 | 25(1") | 8
19 | PW-801M | 60(at Ht 12m) | 38 | 1Phase 220V 60Hz | 750 | Clean Water | 2 | 3400 | □ Closed ■ Westo □ Open | 40(1 1/2") | GC150 | C3771BD | STS410 | GC200 | 0 | 11 | 35 | 60 | 62 | 73 | 66 | 46 | 26 | 12 | 1.13 | 1.03 | 0.8 | 0.57 | 0.45 | 0 | 11.5 | 32.89 | 44.39 | 27.15 | 40(1 1/2") | 8
20 | PW-951M | 75(at Ht 12m) | 38 | 1Phase 220V 60Hz | 950 | Clean Water | 2 | 3400 | □ Closed ■ Westo □ Open | 40(1 1/2") | GC150 | C3771BD | STS410 | GC200 | 0 | 18.6 | 56.9 | 78.4 | 82.5 | 73 | 63 | 33 | 12 | 3 | 1.58 | 1.33 | 0.88 | 0.63 | 0.52 | 0 | 14.37 | 34.9 | 24.3 | 7.76 | 40(1 1/2") | 8
21 | PW-804MA | 45(at Ht 12m) | 33 | 1Phase 220V 60Hz | 750 | Clean Water | 2 | 3400 | □ Closed ■ Westo □ Open | 40(1 1/2") | GC150 | C3771BD | STS410 | GC200 | 0 | 11 | 21 | 46 | 50 | 74 | 61 | 46 | 16 | 12 | 0.99 | 0.89 | 0.76 | 0.54 | 0.52 | 0 | 12.26 | 20.62 | 22.15 | 18.88 | 40(1 1/2") | 8
22 | PW-1604M | 50(at Ht 52m) | 63 | 1Phase 220V 60Hz | 1500 | Clean Water | 2 | 3400 | □ Closed ■ Westo □ Open | 40(1 1/2") | GC150 | C3771BD | STS410 | GC200 | 0 | 16.8 | 52.8 | 58.4 | 61.2 | 101 | 86 | 56 | 46 | 26 | 2.71 | 2.42 | 1.85 | 1.67 | 1.27 | 0 | 9.74 | 25.99 | 26.26 | 20.38 | 40(1 1/2") | 8
23 | PW-1605I | 50(at Ht 52m) | 63 | 3Phase 220V/380V 60Hz | 1500 | Clean Water | 2 | 3400 | □ Closed ■ Westo □ Open | 40(1 1/2") | GC150 | C3771BD | STS410 | GC200 | 0 | 9.1 | 42.3 | 58.1 | 62.8 | 105 | 96 | 66 | 46 | 16 | 3.21 | 3 | 2.28 | 1.81 | 1.05 | 0 | 4.75 | 19.99 | 24.07 | 15.6 | 40(1 1/2") | 8
24 | PW-1602MA | 45(at Ht 40m) | 53 | 1Phase 220V 60Hz | 1500 | Clean Water | 2 | 3400 | □ Closed ■ Westo □ Open | 40(1 1/2") | GC150 | C3771BD | STS410 | GC200 | 0 | 18 | 50 | 60 | 64 | 96 | 82 | 52 | 26 | 7 | 2.36 | 2.09 | 1.68 | 1.21 | 0.84 | 0 | 12.09 | 25.27 | 20.94 | 8.68 | 40(1 1/2") | 8
25 | PW-1603UA | 45(at Ht 40m) | 53 | 3Phase 380V 60Hz | 1500 | Clean Water | 2 | 3400 | □ Closed ■ Westo □ Open | 40(1 1/2") | GC150 | C3771BD | STS410 | GC200 | 0 | 16.1 | 43.9 | 52 | 55 | 96 | 81 | 56 | 31 | 21 | 2.88 | 2.52 | 1.92 | 1.32 | 1.09 | 0 | 8.44 | 20.85 | 19.84 | 17.34 | 40(1 1/2") | 8
26 | PWN-262M | 20(at Ht 12m) | 32 | 1Phase 220V 60Hz | 250 | Clean Water | 2 | 3400 | □ Closed ■ Westo □ Open | 15(1/2") | GC150 | C3771BD | STS410 | GC200 | 0 | 4.5 | 12.5 | 20 | 27.7 | 43 | 35 | 22 | 12 | 3 | 0.31 | 0.27 | 0.22 | 0.17 | 0.15 | 0 | 9.47 | 20.04 | 22.36 | 9.23 | 15(1/2") | 8
27 | PWN-263M | 20(at Ht 12m) | 32 | 1Phase 220V 60Hz | 250 | Clean Water | 2 | 3400 | □ Closed ■ Westo □ Open | 15(1/2") | GC150 | C3771BD | STS410 | GC200 | 0 | 4.9 | 16 | 24.1 | 35 | 51.1 | 40 | 25 | 12 | 1 | 0.39 | 0.33 | 0.26 | 0.18 | 0.15 | 0 | 9.7 | 25.18 | 25.53 | 3.92 | 15(1/2") | 8
28 | PB-135MA | 40(at Ht 0.5m) | 13 | 1Phase 220V 60Hz | 135 | Clean Water | 2 | 3400 | ■ Closed □Westo □ Open | 15(1/2") | GC200+Coating | NORYL | STS410 | C3771BD | Capa1: 0; Capa2: 13.5; Capa3: 24.7; Capa4: 32.3; Capa5: 50.1; Head1: 13.9; Head2: 12; Head3: 10; Head4: 8; Head5: 0.5 | 15(1/2") | 8
29 | PB-168EA | 40(at Ht 0.5m) | 13 | 1Phase 220V 60Hz | 135 | Clean Water | 2 | 3400 | ■ Closed □Westo □ Open | 15(1/2") | GC200+Coating | NORYL | STS410 | C3771BD | Capa1: 0; Capa2: 13.5; Capa3: 24.7; Capa4: 32.3; Capa5: 50.1; Head1: 13.9; Head2: 12; Head3: 10; Head4: 8; Head5: 0.5 | 15(1/2") | 8
30 | PB-260MA | 55(at Ht 0.5m) | 21 | 1Phase 220V 60Hz | 260 | Clean Water | 2 | 3450 | ■ Closed □Westo □ Open | 15(1/2") | GC200+Coating | NORYL | STS410 | C3771BD | Capa1: 0; Capa2: 10; Capa3: 20; Capa4: 40; Capa5: 60; Head1: 23; Head2: 22; Head3: 19; Head4: 12; Head5: 2 | 15(1/2") | 8
31 | PW-2200i | 50(at Ht 52m) | 63 | 3Phase 220V/380V 60Hz | 2200 | Clean Water | 2 | 3400 | □ Closed ■ Westo □ Open | 40(1 1/2") | GC150 | C3771BD | STS410 | GC200 | 0 | 9.1 | 42.3 | 58.1 | 62.8 | 105 | 96 | 66 | 46 | 16 | 3.21 | 3 | 2.28 | 1.81 | 1.05 | 0 | 4.75 | 19.99 | 24.07 | 15.6 | 40(1 1/2") | 8
32 | PW-081E | 21(at Ht=0.5m) | 15 | 1Phase 220V 50Hz | 125 | Clean Water | 2 | 2900 | □ Closed ■ Westo □ Open | 20(3/4") | GC150 | C3771BD | STS410 | GC200 | 0 | 6.5 | 13.3 | 17.9 | 21 | 35 | 25 | 15 | 8 | 1 | 0.35 | 0.29 | 0.23 | 0.18 | 0.16 | 0 | 10.1 | 23.36 | 27.52 | 25.39 | 20(3/4") | 8
33 | PW-2200M | 50(at Ht 52m) | 63 | 1Phase 220V 60Hz | 2200 | Clean Water | 2 | 3400 | □ Closed ■ Westo □ Open | 40(1 1/2") | GC150 | C3771BD | STS410 | GC200 | 0 | 9.1 | 42.3 | 58.1 | 62.8 | 105 | 96 | 66 | 46 | 16 | 3.21 | 3 | 2.28 | 1.81 | 1.05 | 0 | 4.75 | 19.99 | 24.07 | 15.6 | 40(1 1/2") | 8
34 | PW-2200MA | 45(at Ht 40m) | 53 | 1Phase 220V 60Hz | 2200 | Clean Water | 2 | 3400 | □ Closed ■ Westo □ Open | 40(1 1/2") | GC150 | C3771BD | STS410 | GC200 | 0 | 18 | 50 | 60 | 64 | 96 | 82 | 52 | 26 | 7 | 2.36 | 2.09 | 1.68 | 1.21 | 0.84 | 0 | 12.09 | 25.27 | 20.94 | 8.68 | 40(1 1/2") | 8