## Datasheet
PUMP DATA SHEET
| Model | PW-601LMA | Title |  |  | Sheet No.
1 | Customer |  |  | Agent No.
2 | Location |  |  | Date Issued
3 | Item No. |  |  | Plant Name
4 | Service |  |  | Quantity |  | Location | ■In, □Out
5 | OPERATING CONDITION
6 | Liquid | Water | Flow | 40 | ℓ/min at Ht=10m | NPSHav | mAq
7 | Pumping Temp | 0~40 ℃ | Suct.Head | 8 | m | Concentration | %
8 | Sp. Gr. @P.T | 1 | Disch.Press | 22 | m | Solid
9 | Vap. Press @P.T | Kg/㎠A | Total Head | 30 | m | Corros.or Erros
10 | Visc @P.T | Cp
11 | PERFORMANCE AND CONSTRUCTIONS |  |  |  |  | MATERIALS
12 | ■ Horizontal | □ Vertical | Efficiency | 25 | % | (Parts' Name) | Symbol(KS)
13 | Number of Stages | 1 Stage | Rated Power | 600 | W | Impeller | C3771BD
14 | Speed | 3400 rpm | NPSHre |  | mAq | Impeller Cover | C3771BD
15 | Rotation | □ CW, ■ CCW | Column Head |  | m | Shaft | STS410
16 | Flange | Size(Dia) | Rating | Face | Position | Casing | GC150
17 | Suction | 30mm |  | ■ FF, □ RF | □End □Top ■Side | Flange | GC200
18 | Discharge | 30mm |  | ■ FF, □ RF | □Top, ■Side
19 | Impeller Type | Wetco Impeller | ■Single Suct. | □Double Suct. | HYDROSTATIC
20 | Flow Direction | ■ Radial | □ Mixed | □ Axial | Casing | 6 Kg/㎠ | 3 Min.
21 | Shaft Seal | □ G/Packing | ■ M/Seal |  | Pressure Tank | 8.5 Kg/㎠ | 3 Min.
22 | Shaft Sleeve | □Yes, ■No
23 | Mounting | ■ Foot | □ Centerline | □ Bracket | TESTING
24 | Lubrication Type | ■ Grease | □ Oil Bath |  | (Items) | (self test) | (witness)
25 | Cooling | □ Stuff.Box | □B/R Housing | ■ No. Cooling | Run Perform. | ■ Yes □ No | □Yes ■No
26 | Radial Bearings | 6202ZZ | Thrust Bearing | 6202ZZ | Hydrostatic | ■ Yes □ No | □Yes ■No
27 | PUMP DRIVER |  |  |  |  | SPARE PARTS
28 | Motor | V/Phase/Hz | 220 | 1 | 60 | Impeller | Set(S)
29 | Maker | WILO-LG PUMPS LTD. |  |  |  | Shaft | Set(S)
30 | Type | ODP |  |  |  | Shaft Sleeve | Set(S)
31 | Power | 600W |  |  |  | Casing Ring | Set(S)
32 | Pole & Speed | 2 p 3400 rpm | Insulation | □ B | ■ E | Bearing(R+T) | Set(S)
33 | ACCESSORIES |  |  |  |  | Bearing(Journal) | Set(S)
34 | ■Base Plate | □ Cast Iron | □ Steel Plate |  | □ Drain Rim | M/Seal | Set(S)
35 | □Foundation Bolts & Nuts |  |  |  |  | Casing Gasket | Set(S)
36 | Coupling | □ Sun Flex | □ WOODS | □ Grid | ■No | Oil Seal | Set(S)
37 | □Press. Gauge | □Suct.Vacuum □Suct.Compound □Suct.Press ■Disch.Press □No |  |  |  | Coupling | Set(S)
38 | ■Collar or Plug for Drain & Air Vent. |  |  |  |  | Coupling Rubber | Set(S)
39 | □Sealing Flushing Pipe |  | □ Cooling Piping | ■No |  | Name Plate | Set(S)
40 |  | Maker | N.E.K | Model & Size | Φ 15 | Spring | 1 Set(S)
41 | Mechanical Seal | Type | EA103-15 | Cooler | □Yes, ■No | WEIGHT
42 | [5 empty] | Pump / Bed | Kg
43 | □ Companion Flange |  |  |  |  | Driver | Kg
44 | □ Special Tools |  |  |  |  | Total Wt. | 34 Kg

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
PUMP | CAPACITY | ℓ/min | 40(at=10m) |  | MOTOR | OUTPUT |  |  |  | W | 600
| TOTAL HEAD | m | 30 |  |  | VOLTAGE |  |  |  | V | 220
| SUCTION FLANGE | mm | Ø | 30 |  | FREQUENCY |  |  |  | Hz | 60
| DISCHARGE FLANGE | mm | Ø | 30 |  | No. OF REVOLUTION |  |  |  | r.p.m | 3400
| LIQUID | WATER |  |  |  | TYPE |  |  |  | 1 PHASE INDUCTION
| MAKER | WILO-LG |  |  |  | MAKER |  |  |  | WILO-LG
[7 empty] | TYPE |  | WESTCO PUMP
[7 empty] | MODEL |  | PW-601LMA
SERVICE
SCALE : N/S
OUTLINE DRAWING
of PW TYPE
232
270
256
295
540
340
620

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO. | PARTS NAME | MATERIALS |  |  |  | Q'ty(EA)
1 | MOTOR | - |  |  |  | 1
2 | CAPACITOR COVER | ABS |  |  |  | 1
3 | IMPELLER | C3771BD |  |  |  | 1
4 | CASING | GC150 |  |  |  | 1
5 | DISCHARGE FLANGE | GC200 |  |  |  | 1
6 | GASKET | NBR |  |  |  | 2
7 | SUCTION FLANGE | GC200 |  |  |  | 1
8 | CHECK VALVE | - |  |  |  | 1
9 | FLEXIBLE HOSE | - |  |  |  | 1
10 | MECHANICAL SEAL | CARBON+CERAMIC |  |  |  | 1
11 | PRESSURE TANK | - |  |  |  | 1
12 | BASE PLATE | SPCC |  |  |  | 1
|  |  | TYPE |  | WESTCO PUMP
|  |  | MODEL |  | PW-601LMA
SERVICE
SCALE:N/S
SECTIONAL DRAWING
of PW TYPE
1
2
3
4
6
7
8
9
10
11
12
5

## Test Report
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 7 | 12 | 17 | 22 | 27 | 36 | 41
Dis. Head | (m) | 43.4 | 35 | 30 | 25 | 20 | 15 | 6 | 0.9
Suc. Head | (m) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Speed Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Head | (m) | 49.4 | 41 | 36 | 31 | 26 | 21 | 12 | 6.9
Water Power | (㎾) | 0 | 0.046781 | 0.070416 | 0.085901 | 0.093236 | 0.092421 | 0.070416 | 0.046113
Shaft Power | (㎾) | 0.60654 | 0.53526 | 0.4917 | 0.45276 | 0.41118 | 0.38148 | 0.3267 | 0.297
Pump Eff. | (%) | 0 | 8.7399 | 14.3209 | 18.9727 | 22.6752 | 24.227 | 21.5537 | 15.5262
Speed | (rpm) | 3357 | 3382 | 3404 | 3427 | 3446 | 3465 | 3492 | 3502
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 4.34 | 3.87 | 3.6 | 3.37 | 3.11 | 2.97 | 2.68 | 2.54
Motor Input | (㎾) | 0.919 | 0.811 | 0.745 | 0.686 | 0.623 | 0.578 | 0.495 | 0.45
Motor Eff. | (%) | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  | 7: MOTOR SPECIFICATION; 27: TEST CONDITION
Capacity | 32 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.6 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 12 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 | 30 | 30
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) |  | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 66 | Maker | WILO | Electric | 22 | 21
Item No. |  |  | Serial No. | 표준품 | Inspector | K.I.H | Run (Hr) | B/R (℃) | Test Date
Model | PW-601LMA | 7: Customer; 27: 1
Checked By |  | 17: Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification