## Datasheet
PUMP DATA SHEET
| Model | PW-952M | Title |  |  | Sheet No.
1 | Customer |  |  | Agent No.
2 | Location |  |  | Date Issued
3 | Item No. |  |  | Plant Name
4 | Service |  |  | Quantity |  | Location | ■In, □Out
5 | OPERATING CONDITION
6 | Liquid | Water | Flow | 75 ℓ/min | at Ht=12m | NPSHav | mAq
7 | Pumping Temp | 0~40 ℃ | Suct.Head | 8 | m | Concentration | %
8 | Sp. Gr. @P.T | 1 | Disch.Press | 30 | m | Solid
9 | Vap. Press @P.T | Kg/㎠A | Total Head | 38 | m | Corros.or Erros
10 | Visc @P.T | Cp
11 | PERFORMANCE AND CONSTRUCTIONS |  |  |  |  | MATERIALS
12 | ■ Horizontal | □ Vertical | Efficiency | 20 | % | (Parts' Name) | Symbol(KS)
13 | Number of Stages | 1 Stage | Rated Power | 950 | W | Impeller | C3771BD
14 | Speed | 3400 rpm | NPSHre |  | mAq | Impeller Cover | C3771BD
15 | Rotation | □ CW, ■ CCW | Column Head |  | m | Shaft | STS410
16 | Flange | Size(Dia) | Rating | Face | Position | Casing | GC150
17 | Suction | 40mm |  | ■ FF, □ RF | □End □Top ■Side | Flange | GC200
18 | Discharge | 40mm |  | ■ FF, □ RF | □Top, ■Side | Chamber | GC150
19 | Impeller Type | Wetco Impeller | ■Single Suct. | □Double Suct. | HYDROSTATIC
20 | Flow Direction | ■ Radial | □ Mixed | □ Axial | Casing | 6 Kg/㎠ | 3 Min.
21 | Shaft Seal | □ G/Packing | ■ M/Seal |  | Pressure Tank | Kg/㎠ | Min.
22 | Shaft Sleeve | □Yes, ■No
23 | Mounting | ■ Foot | □ Centerline | □ Bracket | TESTING
24 | Lubrication Type | ■ Grease | □ Oil Bath |  | (Items) | (self test) | (witness)
25 | Cooling | □ Stuff.Box | □B/R Housing | ■ No. Cooling | Run Perform. | ■ Yes □ No | □Yes ■No
26 | Radial Bearings | 6204ZZ | Thrust Bearing | 6203ZZ | Hydrostatic | ■ Yes □ No | □Yes ■No
27 | PUMP DRIVER |  |  |  |  | SPARE PARTS
28 | Motor | V/Phase/Hz | 220 | 1 | 60 | Impeller | Set(S)
29 | Maker | WILO PUMPS LTD. |  |  |  | Shaft | Set(S)
30 | Type | ODP |  |  |  | Shaft Sleeve | Set(S)
31 | Power | 950W |  |  |  | Casing Ring | Set(S)
32 | Pole & Speed | 2 p 3400 rpm | Insulation | ■ B | □ E | Bearing(R+T) | Set(S)
33 | ACCESSORIES |  |  |  |  | Bearing(Journal) | Set(S)
34 | ■Base Plate | □ Cast Iron | □Steel Plate | ■Plastic Plate | □ Drain Rim | M/Seal | Set(S)
35 | □Foundation Bolts & Nuts |  |  |  |  | Casing Gasket | Set(S)
36 | Coupling | □ Sun Flex | □ WOODS | □ Grid | ■No | Oil Seal | Set(S)
37 | □Press. Gauge | □Suct.Vacuum □Suct.Compound □Suct.Press □Disch.Press □No |  |  |  | Coupling | Set(S)
38 | ■Collar or Plug for Drain & Air Vent. |  |  |  |  | Coupling Rubber | Set(S)
39 | □Sealing Flushing Pipe |  | □ Cooling Piping | ■No |  | Name Plate | Set(S)
40 |  | Maker | N.E.K | Model & Size | Φ 15 | Spring | 1 Set(S)
41 | Mechanical Seal | Type | EA103-15 | Cooler | □Yes, ■No | WEIGHT
42 | [5 empty] | Pump / Bed | Kg
43 | □ Companion Flange |  |  |  |  | Driver | Kg
44 | □ Special Tools |  |  |  |  | Total Wt. | 23 Kg
s

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
TYPE |  | WESTCO PUMP
MODEL |  | PW-952M
SERVICE
SCALE : N/S
OUTLINE DRAWING
of PW TYPE

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO. | PARTS NAME | MATERIALS |  |  |  | Q'ty(EA)
1 | MOTOR | - |  |  |  | 1
2 | CAPACITOR COVER | ABS |  |  |  | 1
3 | IMPELLER | C3771BD |  |  |  | 1
4 | CASING | GC150 |  |  |  | 1
5 | DISCHARGE FLANGE | GC200 |  |  |  | 1
6 | GASKET | NBR |  |  |  | 2
7 | SUCTION FLANGE | GC200 |  |  |  | 1
8 | CHECK VALVE | - |  |  |  | 1
9 | MECHANICAL SEAL | CARBON+CERAMIC |  |  |  | 1
10 | BASE PLATE | HDPE |  |  |  | 1
11 | AIR CHAMBER | GC150 |  |  |  | 1
|  |  | TYPE |  | WESTCO PUMP
|  |  | MODEL |  | PW-952M
SERVICE
SCALE:N/S
SECTIONAL DRAWING
of PW TYPE
1
2
3
4
6
7
8
9
10
11
5

## Test Report
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 21.6 | 33.1 | 45.1 | 56.1 | 67.9 | 78.8 | 82.9
Dis. Head | (m) | 76.8 | 60 | 50 | 40 | 30 | 20 | 9 | 0.1
Suc. Head | (m) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Speed Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Head | (m) | 79.8 | 63 | 53 | 43 | 33 | 23 | 12 | 3.1
Water Power | (㎾) | 0 | 0.22181 | 0.28595 | 0.31611 | 0.30176 | 0.25456 | 0.15413 | 0.041889
Shaft Power | (㎾) | 1.7411 | 1.3999 | 1.233 | 1.0721 | 0.92678 | 0.78374 | 0.63101 | 0.52821
Pump Eff. | (%) | 0 | 15.8452 | 23.1919 | 29.486 | 32.5603 | 32.4798 | 24.4262 | 7.9305
Speed | (rpm) | 3180 | 3285 | 3342 | 3387 | 3426 | 3462 | 3500 | 3524
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 10.6 | 8.42 | 7.35 | 6.37 | 5.59 | 4.72 | 3.82 | 3.21
Motor Input | (㎾) | 2.337 | 1.879 | 1.655 | 1.439 | 1.244 | 1.052 | 0.847 | 0.709
Motor Eff. | (%) | 74.5 | 74.5 | 74.5 | 74.5 | 74.5 | 74.5 | 74.5 | 74.5
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 75 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.95 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 12 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 | 40 | 40
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) |  | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 74.5 | Maker | WILO | Electric | 30 | 23
Item No. |  |  | Serial No. |  | Inspector | G.I.H | Run (Hr) | B/R (℃) | Test Date
Model | PW-952M |  | Customer |  |  |  | 1
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 220.716 | 220.716 | 220.716 | 220.716 | 220.716 | 220.716 | 220.716 | 220.716
Suc. Head | m | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Suc. Head | m | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Vacuum | mmhg | 220.716 | 220.716 | 220.716 | 220.716 | 220.716 | 220.716 | 220.716 | 220.716
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Data (hidden)
No. | Model | Capa.(ℓ/min.) | Head(m) | Power Supply | Output | Disharge | Pole | RPM | Impeller Type | Suction | Casing Mat'l | Impeller Mat'l | Shaft Mat'l | Flange Mat'l | Capa1 | Capa2 | Capa3 | Capa4 | Capa5 | Head1 | Head2 | Head3 | Head4 | Head5 | SP1 | SP2 | SP3 | SP4 | SP5 | Eff1 | Eff2 | Eff3 | Eff4 | Eff5 | 380V Amp.
1 | PU-756M | 200(at Ht 6m) | 35 | 1Phase 220V 60Hz | 750 | Clean Water | 2 | 3400 | □ Closed ■ Semi-Open □ Open | 50(2") | GC150 | C3771BD | STS410 | GC200 | 0 | 107.7 | 172 | 227.5 | 233 | 21.7 | 18 | 14 | 8 | 6.5 | 0.35 | 0.51 | 0.59 | 0.63 | 0.62 | 0 | 61.83 | 66.51 | 47.21 | 39.59 | 8
2 | PW-K130MA | 200(at Ht 6m) | 35 | 1Phase 220V 60Hz | 750 | Clean Water | 2 | 3400 | □ Closed ■ Semi-Open □ Open | 50(2") | GC150 | C3771BD | STS410 | GC200 | 0 | 107.7 | 172 | 227.5 | 233 | 21.7 | 18 | 14 | 8 | 6.5 | 0.35 | 0.51 | 0.59 | 0.63 | 0.62 | 0 | 61.83 | 66.51 | 47.21 | 39.59 | 8
3 | PW-409MA | 32(at Ht 12m) | 30 | 1Phase 220V 60Hz | 400 | Clean Water | 2 | 3400 | □ Closed ■ Westo □ Open | 30(1 1/4") | GC150 | C3771BD | STS410 | GC200 | 0 | 8.1 | 16.7 | 28.5 | 38 | 55 | 46 | 36 | 21 | 9 | 0.6 | 0.55 | 0.47 | 0.37 | 0.3 | 0 | 11.12 | 20.82 | 26.38 | 18.59 | 8
4 | PW-405M | 40(at Ht 12m) | 36 | 1Phase 220V 60Hz | 400 | Clean Water | 2 | 3400 | □ Closed ■ Westo □ Open | 30(1 1/4") | GC150 | C3771BD | STS410 | GC200 | 0 | 10 | 31 | 41 | 46 | 53 | 46 | 26 | 16 | 9.5 | 0.73 | 0.65 | 0.46 | 0.39 | 0.34 | 0 | 11.48 | 28.68 | 27.55 | 20.94 | 8
5 | PW-804MA | 45(at Ht 12m) | 33 | 1Phase 220V 60Hz | 750 | Clean Water | 2 | 3400 | □ Closed ■ Westo □ Open | 40(1 1/2") | GC150 | C3771BD | STS410 | GC200 | 0 | 15 | 32 | 46 | 50 | 74 | 56 | 34 | 16 | 12 | 0.99 | 0.85 | 0.67 | 0.54 | 0.52 | 0 | 16.14 | 26.51 | 22.15 | 18.88 | 8