## Datasheet
PUMP DATA SHEET
| Model | PWS-350SMA | Title |  |  | Sheet No.
1 | Customer |  |  | Agent No.
2 | Location |  |  | Date Issued
3 | Item No. |  |  | Plant Name
4 | Service |  |  | Quantity |  | Location | ■In, □Out
5 | OPERATING CONDITION
6 | Liquid | Water | Flow | 25 ℓ/min | at Ht=12m | NPSHav | mAq
7 | Pumping Temp | 0~40 ℃ | Suct.Head | 3 | m | Concentration | %
8 | Sp. Gr. @P.T | 1 | Disch.Press | 16 | m | Solid
9 | Vap. Press @P.T | Kg/㎠A | Total Head | 19 | m | Corros.or Erros
10 | Visc @P.T | Cp
11 | PERFORMANCE AND CONSTRUCTIONS |  |  |  |  | MATERIALS
12 | ■ Horizontal | □ Vertical | Efficiency | 25 | % | (Parts' Name) | Symbol(KS)
13 | Number of Stages | 1 Stage | Rated Power | 350 | W | Impeller | C3771BD
14 | Speed | 3400 rpm | NPSHre |  | mAq | Impeller Cover | C3771BD
15 | Rotation | □ CW, ■ CCW | Column Head |  | m | Shaft | STS410
16 | Flange | Size(Dia) | Rating | Face | Position | Casing | GC150
17 | Suction | 25mm |  | ■ FF, □ RF | □End □Top ■Side | Flange | GC200
18 | Discharge | 25mm |  | ■ FF, □ RF | □Top, ■Side | Chamber | GC200
19 | Impeller Type | Centrifugal | ■Single Suct. | □Double Suct. | HYDROSTATIC
20 | Flow Direction | ■ Radial | □ Mixed | □ Axial | Casing | 4 Kg/㎠ | 3 Min.
21 | Shaft Seal | □ G/Packing | ■ M/Seal |  | Pressure Tank | 7.5 Kg/㎠ | 3 Min.
22 | Shaft Sleeve | □Yes, ■No
23 | Mounting | ■ Foot | □ Centerline | □ Bracket | TESTING
24 | Lubrication Type | ■ Grease | □ Oil Bath |  | (Items) | (self test) | (witness)
25 | Cooling | □ Stuff.Box | □B/R Housing | ■ No. Cooling | Run Perform. | ■ Yes □ No | □Yes ■No
26 | Radial Bearings | 6201ZZ | Thrust Bearing | 6201ZZ | Hydrostatic | ■ Yes □ No | □Yes ■No
27 | PUMP DRIVER |  |  |  |  | SPARE PARTS
28 | Motor | V/Phase/Hz | 220 | 1 | 60 | Impeller | Set(S)
29 | Maker | WILO |  |  |  | Shaft | Set(S)
30 | Type | ODP |  |  |  | M/Seal | Set(S)
31 | Power | 350W |  |  |  | Casing | Set(S)
32 | Pole & Speed | 2 p 3400 rpm | Insulation | ■ B | □ E | Valve | Set(S)
33 | ACCESSORIES |  |  |  |  | Union | Set(S)
34 | ■Base Plate | □ Cast Iron | ■ Plastic | □ Steel Plate | □ Drain Rim |  | Set(S)
35 | □Unions | [5 empty] | Set(S)
36 | □Coupling | □ Sun Flex | □ WOODS | □ Grid | ■No |  | Set(S)
37 | □Press. Gauge | □Suct.Vacuum □Suct.Compound □Suct.Press □Disch.Press ■No |  |  |  |  | Set(S)
38 | □Plug for Priming & Screw for Drain | [5 empty] | Set(S)
39 | □Sealing Flushing Pipe |  | □ Cooling Piping | ■No |  |  | Set(S)
40 |  | Maker | N.E.K | Model & Size | Φ12 |  | Set(S)
41 | Mechanical Seal | Type | EA103-12 | Cooler | □Yes, ■No | WEIGHT
42 | [5 empty] | Pump / Bed | Kg
43 | ■ Companion Flange |  |  |  |  | Driver | Kg
44 | □ Special Tools |  |  |  |  | Total Wt. | 13.5Kg

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
TYPE |  | WESTCO PUMP
MODEL |  | PWS-350SMA
SERVICE
SCALE:N/S
OUTLINE DRAWING
of PW TYPE

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO. | PARTS NAME | MATERIALS |  |  |  | Q'ty(EA)
1 | MOTOR | - |  |  |  | 1
2 | MECHANICAL SEAL | CARBON/CERAMIC |  |  |  | 1
3 | IMPELLER | C3771BD |  |  |  | 1
4 | IMPELLER COVER | C3771BD |  |  |  | 1
5 | CAPACITOR | - |  |  |  | 1
6 | HOPPER CAP | C3771BD |  |  |  | 1
7 | PCB | - |  |  |  | 1
8 | TERMINAL BASE | ABS |  |  |  | 1
9 | TERMINAL COVER | ABS |  |  |  | 1
10 | PRESSURE SWITCH | - |  |  |  | 1
11 | SWITCH ASSY | - |  |  |  | 1
12 | VALVE ASSY | NORYL |  |  |  | 1
13 | CHECK VALVE COVER | PBT |  |  |  | 1
14 | FLANGE OVAL | GC200 |  |  |  | 2
15 | PRESSURE TANK | - |  |  |  | 1
16 | FAN | PBT |  |  |  | 1
17 | FAN COVER | ABS |  |  |  | 1
|  |  | TYPE |  | WESTCO PUMP
|  |  | MODEL |  | PWS-350SMA
SERVICE
SCALE:N/S
SECTIONAL DRAWING
of PWS TYPE

## Test Report
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 7.1 | 14.8 | 18.1 | 22 | 30 | 36.9 | 40.8
Dis. Head | (m) | 32 | 27 | 21 | 18 | 15 | 9 | 3 | 0
Suc. Head | (m) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Speed Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Head | (m) | 35 | 30 | 24 | 21 | 18 | 12 | 6 | 3
Water Power | (㎾) | 0 | 0.034719 | 0.057898 | 0.061956 | 0.064548 | 0.05868 | 0.036088 | 0.019951
Shaft Power | (㎾) | 0.28728 | 0.30744 | 0.2709 | 0.25389 | 0.23373 | 0.19845 | 0.1701 | 0.15624
Pump Eff. | (%) | 0 | 11.2929 | 21.3723 | 24.4028 | 27.6165 | 29.5692 | 21.2159 | 12.7696
Speed | (rpm) | 3312 | 3355 | 3405 | 3424 | 3450 | 3483 | 3511 | 3522
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 2.77 | 2.48 | 2.17 | 2.04 | 1.88 | 1.63 | 1.41 | 1.3
Motor Input | (㎾) | 0.456 | 0.488 | 0.43 | 0.403 | 0.371 | 0.315 | 0.27 | 0.248
Motor Eff. | (%) | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 25 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.35 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 12 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 | 25 | 25
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 2.3 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 63 | Maker | WILO | Electric | 22 | 18
Item No. |  |  | Serial No. | 표준품 | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PWS-350SMA |  | Customer |  |  |  | 1
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification